## Sheet2
Pipework Material |  | Copper TableX R290
| Flow Rate (kg/s) q | Temperature (deg C) | Nominal Pipe Size (mm) | Internal Diameter di (mm) | Relative Roughness k | Velocity (m/s) c | Velocity Pressure (Pa) Pv | Reynolds Number Re | lamda λ | Pressure Drop (Pa/m) ∆P | Equivalent Length (m) le
| 0.35 | 65 | 35 | 33 | 0.0015 | 0.41735 | 85.3931 | 28916.6077 | 0.023606 | 61.0839 | 1.398
Results obtained using the formulas below, in accordance with CIBSE guide C (2007) section 4:
Pv = 1/2 Ρ v2 (density linked to water temperature)
Re = (c x di) / v (v = water dynamic viscosity)
1 / (√λ) = -1.8 log ((6.9 / Re) + ((k / d) / 3.71)1.1
∆P = λ (1 / di) 1/2 Ρ v2
| le = Pv / ∆P (CIBSE Guide C Flow of fluids in pipes and ducts 2004) |  |  |  |  | BASED on INDEX RUN
| PROJECT TITLE: | LLOYDS BUILDING - LEEDS Existing Building, 4Xfloor X Offices |  |  |  |  | PIPE MATERIAL: | Copper
| PIPE | ACTUAL HEAT |  | FLOW | PIPE | ACTUAL PIPE | TOTAL LENGTH | PRESSURE | HEAD LOSS/
| SECTION | REQUIRED (KW) | (+ 5% PIPE LOSSES) | Kg/s | SIZE (mm) | LENGTH | ACTUAL +25% | LOSS/m (Pa) | SECTION (Pa)
| A | 10.5 | 11.025 | 0.23864 | 28 | 10 | 12.5 | 90 | 1125
| Fittings | Comm Set | 5 | 0.10823 | 35 | 1 | 1.25 | 5 | 6.25
| Fittings | Strainers | 1.5 | 0.032468 | 35 | 1 | 1.25 | 1.5 | 1.875
| B | 6.33 | 6.6465 | 0.14386 | 22 | 1 | 1.25 | 120 | 150
| Fittings | Comm Set | 5 | 0.10823 | 35 | 1 | 1.25 | 5 | 6.25
| C | 5.8 | 6.09 | 0.13182 | 22 | 3 | 3.75 | 120 | 450
| Fittings | RADIATORS | 11 | 0.2381 | 35 | 1 | 1.25 | 5 | 6.25
| D | 5.6 | 5.88 | 0.12727 | 22 | 2.2 | 2.75 | 100 | 275
| Fittings | Comm Set | 5 | 0.10823 | 35 | 1 | 1.25 | 5 | 6.25
| E | 3.6 | 3.78 | 0.081818 | 15 | 4.5 | 5.625 | 320 | 1800
| Fittings | Comm Set | 5 | 0.10823 | 35 | 1 | 1.25 | 5 | 6.25
| F | 2.85 | 2.9925 | 0.064773 | 15 | 5 | 6.25 | 200 | 1250
| Fittings | Comm Set | 5 | 0.10823 | 35 | 1 | 1.25 | 5 | 6.25
| G | 2.15 | 2.2575 | 0.048864 | 15 | 0.5 | 0.625 | 120 | 75
| Fittings | Comm Set | 5 | 0.10823 | 35 | 1 | 1.25 | 5 | 6.25
| H | 1.28 | 1.344 | 0.029091 | 15 | 7 | 8.75 | 80 | 700
| Fittings | Comm Set | 5 | 0.10823 | 35 | 1 | 1.25 | 5 | 6.25
| J | 0.89 | 0.9345 | 0.020227 | 15 | 6 | 7.5 | 80 | 600
| Fittings | Comm Set | 5 | 0.10823 | 35 | 1 | 1.25 | 5 | 6.25
|  | 0 | 0 | 0 |  |  | 0 |  | 0
| Fittings | Comm Set | 5 | 0.10823 | 35 | 1 | 1.25 | 5 | 6.25
|  | 0 | 0 | 0 |  |  | 0 |  | 0
| Fittings | Comm Set | 5 | 0.10823 | 35 | 1 | 1.25 | 5 | 6.25
|  | 0 | 0 | 0 |  |  | 0 |  | 0
| Fittings | Comm Set | 5 | 0.10823 | 35 | 1 | 1.25 | 5 | 6.25
|  | 0 | 0 | 0 |  |  | 0 |  | 0
|  | 0 | 0 | 0 |  |  | 0 |  | 0
|  | 0 | 0 | 0 |  |  | 0 |  | 0
|  | 0 | 0 | 0 |  |  | 0 |  | 0
|  | 0 | 0 | 0 |  |  | 0 |  | 0
|  | 0 | 0 | 0 |  |  | 0 |  | 0
|  | 0 | 0 | 0 |  |  | 0 |  | 0
|  | 0 | 0 | 0 |  |  | 0 |  | 0
|  | 0 | 0 | 0 |  |  | 0 |  | 0
|  | 0 | 0 | 0 |  |  | 0 |  | 0
|  | 0 | 0 | 0 |  |  | 0 |  | 0
|  | 0 | 0 | 0 |  |  | 0 |  | 0
|  |  | 0 | 0 |  |  | 0 |  | 0
|  |  | 0 | 0 |  |  | 0 |  | 0
|  |  | 0 | 0 |  |  | 0 |  | 0
[7 empty] | TOTAL HEAD LOSS |  | 6501.875
[7 empty] | TOTAL HEAD LOSS Kpa |  | 6.5019
+20% for plant selection
Note on B6: Insert required mass flow rate (kg/s)
Note on C6: Select mean water temperature (deg C)
Note on D6: select nominal pipe size (mm)
Note on E6: internal pipe diameter for selected nominal size (mm)
Note on F6: relative roughness of internal surface of selected pipework material
Note on C2: Select relevant pipework material

## Sheet3
Pipe Materials: |  |  |  |  | Relative Roughness:
Copper TableX R290 |  |  | Copper TableX R290 |  | 0.0015
Steel Medium Grade |  |  | Steel Medium Grade |  | 0.04
Steel Heavy Grade |  |  | Steel Heavy Grade |  | 0.04
PVC-U (PN 16) |  |  | PVC-U (PN 16) |  | 0.0015
0
0
[5 empty] | 0 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
| Temperature (deg C) | Density (kg/m3) | Dynamic Viscosity | Temperature (deg C) | Kinematic Viscosity |  | Copper TableX R290 | Internal Diameter | Steel Medium Grade | Internal Diameter | Steel Heavy Grade | Internal Diameter | PVC-U (PN 16) | Internal Diameter
| 90 | 965.3 | 0.000314 | 90 | 3.2529e-07 | Copper TableX R29015 | 1: 15; 2: 13.6 | 1
| 82 | 970.6 | 0.000346 | 82 | 3.5648e-07 | Copper TableX R29022 | 1: 22; 2: 20.2 | 2
| 80 | 971.8 | 0.000355 | 80 | 3.653e-07 | Copper TableX R29028 | 1: 28; 2: 26.2 | 3
| 75 | 974.9 | 0.000378 | 75 | 3.8773e-07 | Copper TableX R29035 | 1: 35; 2: 33 | 4
| 70 | 977.7 | 0.000404 | 70 | 4.1321e-07 | Copper TableX R29042 | 1: 42; 2: 40 | 5
| 65 | 980.5 | 0.000467 | 65 | 4.7629e-07 | Copper TableX R29054 | 1: 54; 2: 52 | 6
| 60 | 983.2 | 0.000467 | 60 | 4.7498e-07 | Copper TableX R29067 | 1: 67; 2: 64.3 | 7
| 55 | 985.7 | 0.000504 | 55 | 5.1131e-07 | Copper TableX R29076 | 1: 76; 2: 73.1 | 8
| 50 | 988 | 0.000547 | 50 | 5.5364e-07 | Copper TableX R290108 | 1: 108; 2: 105 | 9
| 45 | 990.2 | 0.000596 | 45 | 6.019e-07 | Copper TableX R290133 | 1: 133; 2: 130 | 10
| 40 | 992.2 | 0.000653 | 40 | 6.5813e-07 | Copper TableX R290159 | 1: 159; 2: 155 | 11
| 35 | 994 | 0.000719 | 35 | 7.2334e-07 | Copper TableX R290219 | 1: 219; 2: 210 | 12
| 30 | 995.6 | 0.000798 | 30 | 8.0153e-07 | Copper TableX R290267 | 1: 267; 2: 261 | 13
| 25 | 997 | 0.00089 | 25 | 8.9268e-07 | Steel Medium Grade15 | 3: 15; 4: 16.2 | 14
| 20 | 998.2 | 0.001002 | 20 | 1.0038e-06 | Steel Medium Grade20 | 3: 20; 4: 21.7 | 15
| 12 | 999.4 | 0.001234 | 12 | 1.2347e-06 | Steel Medium Grade25 | 3: 25; 4: 27.4 | 16
| 10 | 999.7 | 0.001306 | 10 | 1.3064e-06 | Steel Medium Grade32 | 3: 32; 4: 36.1 | 17
| 9 | 999.7 | 0.001344 | 9 | 1.3444e-06 | Steel Medium Grade40 | 3: 40; 4: 42 | 18
| 6 | 999.9 | 0.001471 | 6 | 1.4711e-06 | Steel Medium Grade50 | 3: 50; 4: 53.1 | 19
| 4 | 999.9 | 0.001565 | 4 | 1.5652e-06 | Steel Medium Grade65 | 3: 65; 4: 68.8 | 20
| 0.01 | 999.8 | 0.001782 | 0.01 | 1.7824e-06 | Steel Medium Grade80 | 3: 80; 4: 80.8 | 21
[6 empty] | Steel Medium Grade100 | 3: 100; 4: 105.1 | 22
[6 empty] | Steel Medium Grade125 | 3: 125; 4: 129.7 | 23
[6 empty] | Steel Medium Grade150 | 3: 150; 4: 155.2 | 24
[6 empty] | Steel Medium Grade200 | 3: 200; 4: 211.9 | 25
[6 empty] | Steel Medium Grade250 | 3: 250; 4: 265.8 | 26
[6 empty] | Steel Heavy Grade15 | 5: 15; 6: 15 | 27
[6 empty] | Steel Heavy Grade20 | 5: 20; 6: 20.5 | 28
[6 empty] | Steel Heavy Grade25 | 5: 25; 6: 25.8 | 29
[6 empty] | Steel Heavy Grade32 | 5: 32; 6: 34.5 | 30
[6 empty] | Steel Heavy Grade40 | 5: 40; 6: 40.4 | 31
[6 empty] | Steel Heavy Grade50 | 5: 50; 6: 51.3 | 32
[6 empty] | Steel Heavy Grade65 | 5: 65; 6: 67 | 33
[6 empty] | Steel Heavy Grade80 | 5: 80; 6: 78.8 | 34
[6 empty] | Steel Heavy Grade100 | 5: 100; 6: 103.3 | 35
[6 empty] | Steel Heavy Grade125 | 5: 125; 6: 128.9 | 36
[6 empty] | Steel Heavy Grade150 | 5: 150; 6: 154.4 | 37
[6 empty] | Steel Heavy Grade200 | 5: 200; 6: 211.9 | 38
[6 empty] | Steel Heavy Grade250 | 5: 250; 6: 265.8 | 39
[6 empty] | PVC-U (PN 16)20 | 7: 20; 8: 17 | 40
[6 empty] | PVC-U (PN 16)25 | 7: 25; 8: 21.2 | 41
[6 empty] | PVC-U (PN 16)32 | 7: 32; 8: 27.2 | 42
[6 empty] | PVC-U (PN 16)40 | 7: 40; 8: 34 | 43
[6 empty] | PVC-U (PN 16)50 | 7: 50; 8: 42.6 | 44
[6 empty] | PVC-U (PN 16)63 | 7: 63; 8: 53.6 | 45
[6 empty] | PVC-U (PN 16)75 | 7: 75; 8: 63.8 | 46
[6 empty] | PVC-U (PN 16)90 | 7: 90; 8: 76.6 | 47
[6 empty] | PVC-U (PN 16)110 | 7: 110; 8: 96.8 | 48
[6 empty] | PVC-U (PN 16)125 | 7: 125; 8: 110.2 | 49
[6 empty] | PVC-U (PN 16)140 | 7: 140; 8: 123.4 | 50
[6 empty] | PVC-U (PN 16)160 | 7: 160; 8: 141 | 51
[6 empty] | PVC-U (PN 16)180 | 7: 180; 8: 158.6 | 52