## Pipetulator
[11 empty] | GAS AT max - 1 BAR (1000 mbar) | [8 empty] | GAS AT 1 BAR (1000 mbar)
PIPETULATOR |  |  | WATER | 1 |  | GAS | 2 |  |  |  | PRESSURE Drop for the particular LENGTH OF PIPE |  |  |  | 3 | AVAILABLE GAS for length of Pipe |  |  |  |  | Q = 0.0071 | ^ d⁵ * h
[6 empty] | m³/sec |  |  |  |  | ploss = ƛ ( L / dƞ ) ( p v² / 2 ) |  |  |  |  | DETERMINING the Flow of GAS throguh Pipe | [5 empty] | S * L
|  |  | 79.2 | m³/hour | GAS | 0.022
[6 empty] | Litres per sec | [6 empty] | ( p v² / 2 ) | 2.944 |  | poles formula
Mass Flow Rate |  |  | 22 | kg/s |  | 22 |  |  |  | ƛ = frictional co-efficient |  | 0.5
Pipe Diameter |  |  | 100 | mm |  | inch pipe | [6 empty] | L / dƞ ) | 5.5 |  | Q = | 18.019 | m³/hour |  |  | ^ d⁵ | 10000000000
[6 empty] | 4 |  |  |  | dƞ hydraulic Dia - mtres |  | 0.1 | [9 empty] | 100000
Velocity |  |  | 2.8019 | m/s | GAS to be BETWEEN 6 - 9 m/sec | [7 empty] | answer = | 8.0959 |  | Coeficient of friction |  | 0.0071 |  |  | *h | 80958.8091
Dynamic Pressure |  |  | 3924.2158 | pa | [5 empty] | ploss in pa | [11 empty] | 574.8075
Reynolds Number |  |  | 214481.3934 | [9 empty] | Kpa | 0.0080959 |  | Dia pf pipe |  | 100 | mm
Roughness |  |  | 0.046 | mm |  | GAS or FLUID ***** |  |  |  | p = density of fluid kg/m³ |  | 0.75 | [8 empty] | S * L | 31.9
FDash (Alsthul Approx) |  |  | 0.018366 |  |  | PROPANE 1.32 | [6 empty] | bar | 0.00080959 |  | h = pressure drop |  | 0.80959 | mbar
Friction Factor |  |  | 0.028 |  |  | nat gas 0.75 |  |  |  | v = Veloicty m/sec |  | 2.8019
Pressure Drop / m |  |  | 1098.7804 | pa / m | [8 empty] | mbar = | 0.80959 |  | s = Specific Gravity |  | 0.58 | SG |  | answer | 18.019 | AVALIABLE GAS
[10 empty] | L = Length |  | 55 | TOTAL Pressure Loss | [8 empty] | m³/hour
Fitting K Factor |  |  | 0.2 | [6 empty] | metres | [5 empty] | L = Length |  | 55 | Metres
Fitting Pressure Drop |  |  | 784.8432 | pa | [11 empty] | MAX h = 1 mbar ** pipe length MUST NOT EXCEED 1 mbar or 10% max operating pressure rate
NOTES :- OPERATING PRESSURE = approx 5 - 7 bar (g) = 7000 mbar
[12 empty] | MAX loss = 700 mbar = 10% |  |  |  | NOTE TRANSCO MAX operating pressures | [6 empty] | EXCEPT at the WELL HEAD and some onshore sites
[7 empty] | = INSERT |  |  |  | SUPPLY PRESSURE |  |  | = CALCULATED |  | MAX YELLOW pipe ,. PE100 = 7 bar (100psi) or PE 80 = 5 Bar g (80psi) | [6 empty] | Where pressures can be 75 to 90 barg -use of covered
[11 empty] | AT ALMARAI = 1.5 bar(g) to 1 bar(g) | [11 empty] | CARBON STEEL to CW6 TRANSCO SPEC
Inside building
Not to exceed MAX loss 100 mbar = 10% inside building
WATER DENSITY at TEMPERATURES | [6 empty] | AIR DENSITY AT TEMPERATURES | [7 empty] | Densities, of some common gases can be found in the table below: | [5 empty] | Friction Coefficients for some Common Materials and Materials Combinations
|  |  |  | Convert kW to m3/hour |  |  | Density and Specific Weight of Air at Standard Atmospheric Pressure - SI Units: | [14 empty] | Materials and Material Combinations |  | Static Frictional Coefficient
Temperature | Density | Specific Weight |  | kW / CV(38.7) * 3.6 | [10 empty] | Gas | Formula | Molecular | Density - ρ - | [5 empty] | - μs -
- t - | - ρ - | - γ - |  |  |  |  | Temperature | Density | Specific Weight |  | Density | Specific Weight |  |  |  |  | weight | (kg/m3) | (lb/ft3) |  |  |  |  | Clean and Dry Surfaces | Lubricated and Greasy Surfaces
(oC) | (kg/m3) | (kN/m3) |  | 79.2 | m³/hour |  | - t - | - ρ - | - γ - |  | - ρ - | - γ - |  |  | Acetylene (ethyne) | C2H2 | 26 | 1.0921) | 0.06821) |  |  | Aluminum | Aluminum | 1.05 - 1.35 | 0.3
0 | 999.8 | 9.806 |  |  |  |  | (oC) | (kg/m3) | (N/m3) |  | (kg/m3) | (N/m3) | [5 empty] | 1.1702) | 0.07292) |  |  | Aluminum-bronze | Steel | 0.45
4 | 1000 | 9.807 |  |  |  |  | -40 | 1.514 | 14.85 |  | 1.514 | 14.85 |  |  | Air |  | 29 | 1.2051) | 0.07521) |  |  | Aluminum | Mild Steel | 0.61
10 | 999.7 | 9.804 |  | Convert m3/hour to kW |  |  | -20 | 1.395 | 13.68 |  | 1.395 | 13.68 | [5 empty] | 1.2932) | 0.08062) |  |  | Brake material2) | Cast iron | 0.4
20 | 998.2 | 9.789 |  | m3/hour / 3.6 * CV(38.7) |  |  | 0 | 1.293 | 12.67 |  | 1.293 | 12.67 |  |  | Ammonia | NH3 | 17.031 | 0.7171) | 0.04481) |  |  | Brake material2) | Cast iron (wet) | 0.2
30 | 995.7 | 9.765 |  |  |  |  | 5 | 1.269 | 12.45 |  | 1.269 | 12.45 | [5 empty] | 0.7692) | 0.04802) |  |  | Brass | Steel | 0.35 | 0.19
40 | 992.2 | 9.731 |  | 851.4 | kW |  | 10 | 1.247 | 12.23 |  | 1.247 | 12.23 |  |  | Argon | Ar | 39.948 | 1.6611) | 0.10371) |  |  | Brass | Cast Iron | 0.31)
50 | 988.1 | 9.69 |  |  |  |  | 15 | 1.225 | 12.01 |  | 1.225 | 12.01 | [5 empty] | 1.78372) | 0.1113532) |  |  | Brick | Wood | 0.6
60 | 983.2 | 9.642 |  |  |  |  | 20 | 1.204 | 11.81 |  | 1.204 | 11.81 |  |  | Benzene | C6H6 | 78.11 | 3.486 | 0.20643 |  |  | Bronze | Steel |  | 0.16
70 | 977.8 | 9.589 |  |  |  |  | 25 | 1.184 | 11.61 |  | 1.184 | 11.61 |  |  | Blast furnace gas |  |  | 1.2502) | 0.07802) |  |  | Bronze | Cast Iron | 0.221)
80 | 971.8 | 9.53 |  |  |  |  | 30 | 1.165 | 11.43 |  | 1.165 | 11.43 |  |  | Butane | C4H10 | 58.1 | 2.4891) | 0.15541) |  |  | Bronze - sintered | Steel |  | 0.13
90 | 965.3 | 9.467 |  |  |  |  | 40 | 1.127 | 11.05 |  | 1.127 | 11.05 | [5 empty] | 2.52) | 0.1562) |  |  | Cadmium | Cadmium | 0.5 | 0.05
100 | 958.4 | 9.399 |  |  |  |  | 50 | 1.109 | 10.88 |  | 1.109 | 10.88 |  |  | Butylene (Butene) | C4H8 | 56.11 | 2.504 | 0.1482) |  |  | Cadmium | Chromium | 0.41 | 0.34
[7 empty] | 60 | 1.06 | 10.4 |  | 1.06 | 10.4 |  |  | Carbon dioxide | CO2 | 44.01 | 1.8421) | 0.11501) |  |  | Cadmium | Mild Steel | 0.461)
[7 empty] | 70 | 1.029 | 10.09 |  | 1.029 | 10.09 | [5 empty] | 1.9772) | 0.12342) |  |  | Cast Iron | Cast Iron | 1.1, 0.151) | 0.071)
[7 empty] | 80 | 0.9996 | 9.803 |  | 0.9996 | 9.803 |  |  | Carbon disulphide |  | 76.13 |  |  |  |  | Cast Iron | Oak | 0.491) | 0.0751
[7 empty] | 90 | 0.9721 | 9.533 |  | 0.9721 | 9.533 |  |  | Carbon monoxide | CO | 28.01 | 1.1651) | 0.07271) |  |  | Cast iron | Mild Steel | 0.4, 0.231) | 0.21, 0.1331)
[7 empty] | 100 | 0.9461 | 9.278 |  | 0.9461 | 9.278 | [5 empty] | 1.2502) | 0.07802) |  |  | Car tire | Asphalt | 0.72
[7 empty] | 200 | 0.7461 | 7.317 |  | 0.7461 | 7.317 |  |  | Carbureted Water Gas |  |  |  | 0.048 |  |  | Car tire | Grass | 0.35
[7 empty] | 300 | 0.6159 | 6.04 |  | 0.6159 | 6.04 |  |  | Chlorine | Cl2 | 70.906 | 2.9941) | 0.18691) |  |  | Carbon (hard) | Carbon | 0.16 | 0.12 - 0.14
[7 empty] | 400 | 0.5243 | 5.142 |  | 0.5243 | 5.142 |  |  | Coal gas |  |  | 0.582) |  |  |  | Carbon | Steel | 0.14 | 0.11 - 0.14
[7 empty] | 500 | 0.4565 | 4.477 |  | 0.4565 | 4.477 |  |  | Coke Oven Gas |  |  |  | 0.0342) |  |  | Chromium | Chromium | 0.41 | 0.34
[7 empty] | 1000 | 0.2772 | 2.719 |  | 0.2772 | 2.719 |  |  | Combustion products |  |  | 1.112) | 0.0692) |  |  | Copper-Lead alloy | Steel | 0.22
[15 empty] | Cyclohexane |  | 84.16 |  |  |  |  | Copper | Copper | 1 | 0.08
[15 empty] | Digester Gas (Sewage or Biogas) |  |  |  | 0.062 |  |  | Copper | Cast Iron | 1.05, 0.291)
[15 empty] | Ethane | C2H6 | 30.07 | 1.2641) | 0.07891) |  |  | Copper | Mild Steel | 0.53, 0.361) | 0.181)
[15 empty] | Ethyl Alcohol |  | 46.07 |  |  |  |  | Diamond | Diamond | 0.1 | 0.05 - 0.1
[15 empty] | Ethyl Chloride |  | 64.52 |  |  |  |  | Diamond | Metal | 0.1 - 0.15 | 0.1
[15 empty] | Ethylene | C2H4 | 28.03 | 1.2602) | 0.07862) |  |  | Glass | Glass | 0.9 - 1.0, 0.41) | 0.1 - 0.6,
[15 empty] | Helium | He | 4.02 | 0.16641) | 0.010391) | [5 empty] | 0.09-0.121)
[18 empty] | 0.17852) | 0.0111432) |  |  | Glass | Metal | 0.5 - 0.7 | 0.2 - 0.3
[15 empty] | N-Heptane |  | 100.2 |  |  |  |  | Glass | Nickel | 0.78 | 0.56
[15 empty] | Hexane |  | 86.17 |  |  |  |  | Graphite | Steel | 0.1 | 0.1
[15 empty] | Hydrogen | H2 | 2.016 | 0.08992) | 0.00562) |  |  | Graphite | Graphite (in vacuum) | 0.5 - 0.8
[15 empty] | Hydrochloric Acid |  | 36.47 | 1.632) |  |  |  | Graphite | Graphite | 0.1 | 0.1
[15 empty] | Hydrogen Chloride | HCl | 36.5 | 1.5281) | 0.09541) |  |  | Hemp rope | Timber | 0.5
[15 empty] | Hydrogen Sulfide | H2S | 34.076 | 1.4341) | 0.08951) |  |  | Horseshoe | Rubber | 0.68
[15 empty] | Krypton |  |  | 3.742) |  |  |  | Horseshoe | Concrete | 0.58
[15 empty] | Methane | CH4 | 16.043 | 0.6681) | 0.04171) |  |  | Ice | Ice | 0.02 - 0.09
[18 empty] | 0.7172) | 0.04472) |  |  | Ice | Wood | 0.05
[15 empty] | Methyl Alcohol |  | 32.04 |  |  |  |  | Ice | Steel | 0.03
[7 empty] | propane |  |  |  | 1.3174 | 70% propane |  |  | Methyl Butane |  | 72.15 |  |  |  |  | Iron | Iron | 1 | 0.15 - 0.20
[15 empty] | Methyl Chloride |  | 50.49 |  |  |  |  | Lead | Cast Iron | 0.431)
[15 empty] | Natural gas |  | 19.5 | 0.7 - 0.92) | 0.044 - 0.0562) |  |  | Leather | Oak | 0.61, 0521
[15 empty] | Neon | Ne | 20.179 | 0.89992) | 0.0561792) |  |  | Leather | Metal | 0.4 | 0.2
[15 empty] | Nitric oxide | NO | 30 | 1.2491) | 0.07801) |  |  | Leather | Wood | 0.3 - 0.4
[15 empty] | Nitrogen | N2 | 28.02 | 1.1651) | 0.07271) |  |  | Leather | Clean Metal | 0.6
[18 empty] | 1.25062) | 0.0780722) |  |  | Leather fiber | Cast iron | 0.31
[15 empty] | Nitrogen Dioxide | NO2 | 46.006 |  |  |  |  | Leather fiber | Aluminum | 0.3
[15 empty] | N-Octane |  | 114.22 |  |  |  |  | Magnesium | Magnesium | 0.6 | 0.08
[15 empty] | Nitrous Oxide | N2O | 44.013 |  | 0.114 |  |  | Masonry | Brick | 0.6 - 0.7
[15 empty] | Nitrous Trioxide | NO3 | 62.005 |  |  |  |  | Nickel | Nickel | 0.7 - 1.1, | 0.28, 0.121)
[15 empty] | Oxygen | O2 | 32 | 1.3311) | 0.08311) |  |  |  |  | 0.531)
[18 empty] | 1.42902) | 0.0892102) |  |  | Nickel | Mild Steel | 0.641) | 0.1781)
[15 empty] | Ozone | O3 | 48 | 2.142) | 0.125 |  |  | Nylon | Nylon | 0.15 - 0.25
[15 empty] | N-Pentane |  | 72.15 |  |  |  |  | Oak | Oak (parallel grain) | 0.62, 0.481)
[15 empty] | Iso-Pentane |  | 72.15 |  |  |  |  | Oak | Oak (cross grain) | 0.54, 0.321 | 0.0721
[15 empty] | Propane | C3H8 | 44.09 | 1.8821) | 0.11751) |  |  | Paper | Cast Iron | 0.2
[15 empty] | Propene (propylene) | C3H6 | 42.1 | 1.7481) | 0.10911) |  |  | Phosphor-bronze | Steel | 0.35
[15 empty] | R-11 |  | 137.37 |  |  |  |  | Platinum | Platinum | 1.2 | 0.25
[15 empty] | R-12 |  | 120.92 |  |  |  |  | Plexiglas | Plexiglas | 0.8 | 0.8
[15 empty] | R-22 |  | 86.48 |  |  |  |  | Plexiglas | Steel | 0.4-0.5 | 0.4 - 0.5
[15 empty] | R-114 |  | 170.93 |  |  |  |  | Polystyrene | Polystyrene | 0.5 | 0.5
[15 empty] | R-123 |  | 152.93 |  |  |  |  | Polystyrene | Steel | 0.3-0.35 | 0.3 - 0.35
[15 empty] | R-134a |  | 102.03 |  |  |  |  | Polythene | Steel | 0.2 | 0.2
[15 empty] | Sasol |  |  |  | 0.032 |  |  | Polystyrene | Polystyrene | 0.5 | 0.5
[15 empty] | Sulfur | S | 32.06 |  | 0.135 |  |  | Rubber | Rubber | 1.16
[15 empty] | Sulfur Dioxide | SO2 | 64.06 | 2.2791) | 0.17031) |  |  | Rubber | Cardboard | 0.5 - 0.8
[18 empty] | 2.9262) | 0.18282) |  |  | Rubber | Dry Asphalt | 0.9 (0.5 - 0.8)1)
[15 empty] | Sulfur Trioxide | SO3 | 80.062 |  |  |  |  | Rubber | Wet Asphalt | 0.25 - 0.751)
[15 empty] | Sulfuric Oxide | SO | 48.063 |  |  |  |  | Rubber | Dry Concrete | 0.6 - 0.851)
[15 empty] | Toluene | C7H8 | 92.141 | 4.111 | 0.2435 |  |  | Rubber | Wet Concrete | 0.45 - 0.751)
[15 empty] | Water Vapor, steam | H2O | 18.016 | 0.804 | 0.048 |  |  | Silver | Silver | 1.4 | 0.55
[15 empty] | Water gas (bituminous) |  |  |  | 0.054 |  |  | Sapphire | Sapphire | 0.2 | 0.2
[15 empty] | Xenon |  |  | 5.862) |  |  |  | Silver | Silver | 1.4 | 0.55
[22 empty] | Skin | Metals | 0.8 - 1.0
[22 empty] | Steel | Steel | 0.5 - 0.8 | 0.16
[22 empty] | Straw Fiber | Cast Iron | 0.26
[22 empty] | Straw Fiber | Aluminum | 0.27
[22 empty] | Tarred fiber | Cast Iron | 0.15
[22 empty] | Tarred fiber | Aluminum | 0.18
[22 empty] | Teflon | Teflon | 0.04 | 0.04, 0.041)
[22 empty] | Teflon | Steel | 0.05 - 0.2
[22 empty] | Tungsten Carbide | Steel | 0.4-0.6 | 0.1 - 0.2
[22 empty] | Tungsten Carbide | Tungsten Carbide | 0.2 - 0.25 | 0.12
[22 empty] | Tungsten Carbide | Copper | 0.35
[22 empty] | Tungsten Carbide | Iron | 0.8
[22 empty] | Tin | Cast Iron | 0.321)
[22 empty] | Tire, dry | Road, dry | 1
[22 empty] | Tire, wet | Road, wet | 0.2
[22 empty] | Wood | Clean Wood | 0.25 - 0.5
[22 empty] | Wood | Wet Wood | 0.2
[22 empty] | Wood | Clean Metal | 0.2 - 0.6
[22 empty] | Wood | Wet Metals | 0.2
[22 empty] | Wood | Stone | 0.2 - 0.4
[22 empty] | Wood | Concrete | 0.62
[22 empty] | Wood | Brick | 0.6
[22 empty] | Wood - waxed | Wet snow | 0.14, 0.11)
[22 empty] | Wood - waxed | Dry snow | 0.041)
[22 empty] | Zinc | Cast Iron | 0.85, 0.211)
[22 empty] | Zinc | Zinc | 0.6 | 0.04

## Circular Ductulator
DUCTULATOR
Volume Flow Rate | 0.04 | m³/s
Hydraulic Diameter | 150 | mm
Velocity | 2.2635 | m/s
Dynamic Pressure | 3.0742 | pa
Reynolds Number | 18862.8081
Roughness | 0.15 | mm
FDash (Alsthul Approx) | 0.028655
Friction Factor | 0.028655
Pressure Drop | 0.58727 | pa
Fitting K Factor | 0.3
Fitting Pressure Drop | 0.92225 | pa

## Rectangular Ductulator
DUCTULATOR |  |  | DUCTULATOR
Volume Flow Rate | 1 | m³/s | Volume Flow Rate | 0.5 | m³/s
Duct Width | 600 | mm | Duct Width | 350 | mm
Duct Height | 300 | mm | Duct Height | 300 | mm
Hydraulic Diameter | 461.7485 | mm | Hydraulic Diameter | 356.6329 | mm
Velocity | 5.9717 | m/s | Velocity | 5.0054 | m/s
Dynamic Pressure | 21.3968 | pa | Dynamic Pressure | 15.0323 | pa
Reynolds Number | 153190.5893 |  | Reynolds Number | 99171.3406
Roughness | 0.15 | mm | Roughness | 0.15 | mm
FDash (Alsthul Approx) | 0.018316 |  | FDash (Alsthul Approx) | 0.020061
Friction Factor | 0.018316 |  | Friction Factor | 0.020061
Pressure Drop / m | 0.84875 | pa/m | Pressure Drop / m | 0.8456 | pa/m
Fitting K Factor | 0.3 |  | Fitting K Factor | 0.3
Fitting Pressure Drop | 6.419 | pa | Fitting Pressure Drop | 4.5097 | pa

## Notes
Pipe Surface Roughness (CIBSE C4.7)
Material | Roughness (mm)
Non-ferrous drawn piping | 0.0015
Plastic piping | 0.003
Asbestos cement piping | 0.013
Black steel piping (new) | 0.046
Black steel piping (rusted) | 2.5
Properties of Water
Temperature (°C) | 10
density (kg/m³) | 999.73
dynamic viscosity (Pa/m) | 0.001306
kinematic viscosity (m²/s) | 1.3064e-06
Duct Surface Roughness (CIBSE C4.7)
Material | Roughness (mm)
steel | 0.15
neat cement/plaster | 0.25
spiral wound galvanised | 0.075
sheet aluminium | 0.05
plastic | 0.005
brickwork/concrete | 1.3
rough brickwork | 5
Properties of Air (STP)
Temperature (°C) | 20
Barometric Pressure (kPa) | 101.325
density (kg/m³) | 1.2
dynamic viscosity (Pa/m) | 1.8e-05
kinematic viscosity (m²/s) | 1.5e-05
Note on B3: Spreadsheet assumes steel duct
Note on B18: Spreadsheet assumes steel duct
Note on C31: David McAllister: CIBSE Formula C4.38
Note on C32: CIBSE C4.58
Note on C33: dynamic viscosity / density