FIRE PREVENTION I

FIRE & LIFE SAFETY INSPECTIONS FOR THE COMPANY OFFICER

STUDENT SUPPLEMENT

_____________________________________________________________________

SEPTEMBER 2014

Fire Prevention I – Fire & Life Safety Inspections for the Company Officer

Class Description:

Upon completion of this course, the student will have a basic knowledge of the Company Officer certification track and Capstone Task Book process. The student will also be equipped with knowledge and skills related to the Company Officer’s role in fire prevention, the relationship between life safety and building construction, the elements of a quality company inspection program, and how to address complex hazards encountered during an inspection.

Student Profile: Entry level Company Officers, Firefighters

Pre-requisites:  None

Certification:  Fire Officer

Class Size:  40

Student Resources

To participate in this course, students need:

• California Fire Inspector’s Guide

California Fire Chiefs Association, Current Edition

• Fire Prevention Applications for the Company Officer

Fire Protection Publications (FPP), First Edition, ISBN: 978-0-87939-384-7)

Course Objectives

Fire Prevention I provides the students with ability to:

- Describe the purpose and value of a company inspection so that significant fire losses are analyzed where a company inspection could have had an impact and fire and life safety would have been improved.

- Describe the National Fire Incident Reporting System (NFIRS) and the California Incident Reporting System (CAIRS), so that the need for NFIRS reporting is fulfilled.

- Describe the components of a community risk analysis so that the risk is identified and risk control and decision points are initiated.

- Present a fire and life safety education program so that presentation methods for various activities and the five-step public education process are utilized.

- Identify the purpose of and sources for the California Fire Inspector's Guide so that various permit types, abbreviations and definitions, and the layout and format of occupancy requirements are identified.

- Identify their authority and responsibility for performing company inspections so that the correct California statutes within the health and safety and public resource code(s), the California Code of Regulations, Titles 19 and 24, and local codes and ordinances are identified.

- Identify occupancy classifications, target hazards, and potential hazards associated with each occupancy classification, so that all hazards, including hazardous materials, are identified, approved forms are completed, and approved action is initiated.

- Describe fire behavior associated with different types of building construction.

- Develop a pre-incident plan by identifying construction, alarm, detection, and suppression features that contribute to or prevent the spread of fire, heat, and smoke throughout the building or from one building to another.

- Identify the three goals of a company inspection and describe how inspection goals relate to suppression, operations and issues that arise from inconsistent inspections so that all hazards, including hazardous materials, are identified, approved forms are completed, and approved action is initiated.

- Describe the role of the Company Officer in regards to code enforcement and the code enforcement appeal process by determining violation severity, initiating a compliance process, and applying the AHJ’s appeals process

- Identify construction features designed to limit fire, heat, and smoke spread.

- Complete all required records, reports, and forms so that all qualitative information, legal documentation requirements, narrative requirements, and correction plans are documented

- Describe the procedures of the AHJ for conducting fire inspections so that all hazards, including hazardous materials, are identified, approved forms are completed, and approved action is initiated.

- Conduct an inspection of fire alarm detection and notification systems so that all deficiencies are identified, approved forms are completed, and approved action is initiated

- Describe the procedures of the AHJ to conduct an inspection on fire protection system and equipment so that all deficiencies are identified, approved forms are completed, and approved action is initiated.

- Correct fire hazards and code violations so that compliance with identified code violations have been obtained.

- Perform a fire watch so that documentation associated with standby life safety duties are completed.

- Describe the procedures of the AHJ for conducting fire inspection of complex hazards so that all hazards, including hazardous materials, are identified, approved forms are completed, and approved action is initiated.

- Describe the procedures of the AHJ for conducting fire inspections in occupancies containing hazardous materials so that all hazards, including hazardous materials, are identified, approved forms are completed, and approved action is initiated.

- Describe the procedures of the AHJ for conducting fire inspections within the Wildland Urban Interface so that all hazards are identified, approved forms are completed, and approved action is initiated.

Course Content

Unit 1: Introduction

Topic 1-1: Orientation and Administration

Topic 1-2: Company Officer Certification Process

Unit 2: The Company Officer's Role in Fire Prevention

Topic 2-1: Relationship Between Historic and Current Fire Problems

Activity 2-1 Historic Fires

Topic 2-2: National Fire Incident Reporting System

Activity 2-2 – Civilian Fire Fatality Trends

Topic 2-3: Community Risk Analysis

Activity 2-3 – Developing Community Risk Profiles (OPTIONAL)

Topic 2-4: Basic Elements of Fire and Life Safety Education and Public Relations

Topic 2-5: Using The California Fire Inspector's Guide

Activity 2-4 – Using the Inspector’s Guide

Topic 2-6: Authority and Responsibility for Company Inspections and Related Activities

Topic 2-7: Basic Inspection Procedures

Unit 3: Relationship Between Life Safety and Building Construction

Topic 3-1: Occupancy Classifications and Related Hazards

Activity 3-1 –

Topic 3-1-2: Egress (Exit) Systems

Topic 3-2: Building Construction Types and Fire Behavior

Activity 3-2 – Interior Finishes

Topic 3-3: Developing a Pre-Incident Plan

Unit 4: Elements of a Company Inspection Program

Topic 4-1:  Conducting  Fire Inspections

Topic 4-2: Inspecting the Exterior of Buildings

Activity 4-2 – Inspecting the Exterior of Buildings

Topic 4-3: Inspecting the Interior of Buildings

Activity 4-3 – Inspecting the Interior of Buildings

Topic 4-4:  Inspecting Fire Alarm Detection & Notification Systems

Topic 4-5: Inspecting Fire Protection Systems

Topic 4-6: Follow Up Procedures; Code Enforcement & Appeals; Inspection Records, Reports, and Forms

Activity 4-6 – Code Enforcement Violation Ratings

Topic 4-7:  Standby Life Safety Duty

Unit 5: Complex Hazards

Topic 5-1: Inspecting Complex Hazards and Fire Safety Requirements

Activity 5-1-1 – Inspecting Extinguishing Systems

Activity 5-1-2 – Evaluating Characteristics of Ignitable Liquids

Topic 5-2: Hazardous Materials

Activity 5-2-1  MSDS Information Search

Activity 5-2-2 – 704 Placards

Topic 5-3: Inspections in the Wildland Urban Interface Environment

Tests and Grading

Unit Tests

There are four written quizzes during the class. These may be True-False; fill-in the blank questions; or multiple choice. Each quiz will be followed by a group discussion and review. All quizzes count toward the class final grade. A minimum grade of 80% is required to pass each quiz.

Final grades are based on a point system:

- Four quizzes – minimum 80% passing grade

- Completion of all in-class activities and homework

- Attendance

Students must achieve a minimum overall score of 80% to take the State Certification Exam.

Review and Certification Test

The State Certification Test is an open-book fifty (50) question multiple-choice, written examination. Students are allowed to use the California Fire Code as reference during the Certification Exam. The Certification Exam is not related to the final class grade. Examination materials (test book, answer sheet and #2 pencils will be provided by State Fire Training and the Instructor).

Student Expectations:

Students are expected to attend all class periods, come to class prepared for discussions, participate in class and practice Academic Honesty. You are expected to do all of the reading and complete any assigned homework in order to be prepared for the State Certification examination.

Honest Academic Conduct

Honesty and integrity are integral components of the academic process. San Diego Miramar Students are expected to be honest and ethical at all times in their pursuit of academic goals in accordance with Policy 3100, Student Rights, responsibilities and Administrative Due Process. Procedure 3100.3 describes the Academic and Administrative Sanctions for Students who are found to be cheating. A copy of Procedure 3100.3 can be obtained in the Office of the Vice President of Student Services

Class Attendance

Attendance is required for successful course completion.

Most College Districts allow a maximum of 10% (four hours for a forty hour class) of class time absence when advanced notification is given to the instructor.  After missing four hours of class time, you will automatically receive a failing grade in the course. Attendance will be taken every class day and/or session.

Students are responsible for dropping or withdrawing from classes they are no longer attending. Students who remain enrolled in a class beyond the published withdrawal deadline will receive a failing evaluative letter grade.

State Fire Training Attendance Standards

State Fire Training has a rigid attendance policy for all students attending SFT courses -  There are no excused absences from instructional periods. You must attend all instructional time frames specified for the class or you will be ineligible to take the Final/Certification examination.

To insure that students comply with College District and State Fire Training attendance policies and requirements, the following procedures will be implemented and followed:

- Students are required to sign multiple attendance rosters each day throughout class:

- Sign in roster,  beginning of class

- Sign out roster, at lunch

- Sign in roster after lunch

- Sign out roster at end of class

- If you miss a roster event, you will not get credit for that particular class period.

- Missing a roster event makes you ineligible to take the Certification Exam

Smoking Regulations:

All campuses and facilities of the San Diego Community College District, City College, Mesa College, Miramar College, and Continuing Education operate in compliance with the provisions of Government Code 7597 and San Diego Municipal Code section 43.1003(a) regulating smoking in a public place or place of employment. In accordance with Board Policy (BP 0505) Smoke and Tobacco Free District Property smoking and the use of any tobacco product are prohibited on all properties owned or controlled by the District.

Miramar College is committed to creating a clean, healthy working and learning environment for students, faculty, staff and visitors. All students, employees and visitors on the Miramar College property are subject to BP 0505 regulations, which will be strictly enforced at all times.

Alcohol and Drug Use

The classroom and educational environment will be a drug and alcohol free environment.

The San Diego Community College District is committed to providing a drug free environment. District BP 3100 – Code of Conduct states that use, possession, or distribution of narcotics or other controlled substances is prohibited while on the college premises or at college sponsored events. A student may be suspended or expelled for violation of this policy.

If you are suspected of being under the influence of recreational drugs or alcohol, you will be asked to permanently leave the class. There will be no refunds for class fees or textbook costs. This policy includes drug and alcohol use and activities occurring during daily lunch breaks.

Fire Prevention 1 Student Supplement

In addition to the textbooks and/or codes and standards required for Fire Prevention 1 students are required to read the following materials.

Supplemental Materials

• 2-2 Excerpt from the Fire Data Analysis Handbook and USFA Civilian Fire Fatality Report

• 3-3 Preincident Plan Symbols and Documents

• 4-6 Code Enforcement and Appeal Process

• 5-1 Hazardous Processes

• 5-2 When Hazardous Materials are Encountered During a Company Inspection

• 5-3 State of California WUI Regulations

Print materials are included in this student supplement.

2-2 Fire Reporting Systems

Excerpt from the Fire Data Analysis Handbook

Introduction

The primary objective of the National Fire Incident Reporting System is to describe statistical techniques for analyzing data typically collected in fire departments. Motivation for the section stems from the belief that fire departments collect an immense amount of data, but do very little with it. Think for a minute about the reports you complete on incidents. You probably document the type of situation found, action taken, time of alarm, time of arrival, time completed, number of engines responding, number of personnel responding, and many other items. For fires, the list grows even longer to include area of fire origin, form of heat of ignition, type of material involved, and other related facts. Additionally, if civilian or fire fighter injuries occur, other reports need to be completed.

A compelling reason for these reports is a legal requirement for documenting incidents. Victims, insurance companies, lawyers, and many others want copies of reports. Indeed, fire departments maintain files for retrieval of individual reports.

The reports can, however, provide a more beneficial service to fire departments by yielding insight into the nature of fires and injuries in their jurisdiction. Basic information probably is available already. Typically, the number of fires handled last year, the number of fire-related injuries, and the number of fire deaths are tracked. It is another story, however, if more probing questions are asked:

• How many fires took place on Sundays, Mondays, etc.?

• How many fires took place each hour of the day or month of the year?

• What was the average response time to fires?

• How much did response times vary by fire station areas?

• What was the average time spent at the fire scene?

• How much did the average time vary by type of fire?

This handbook describes statistical techniques to turn data into information for answering these types of questions and many others. The techniques range from simple to complex.

Why Data Analysis?

There still may be a question in your mind as to why we should go to all this trouble to analyze data. Many decisions do not require analysis, such as decisions on personnel, grievance proceedings, promotions, and even decisions on how to handle a fire. It is certainly true that fire departments can continue to operate in the same way they always have without doing a lot of analysis.

On the other hand, there are three good reasons for looking closely at the data:

• To gain insights into fire problems

• To improve resource allocation for combating fires

• To identify training needs

Probably the most compelling is that analysis gives insight into fire problems, which in turn can affect operations in the department. One may find, for example, that the average time to fires in an area is six minutes, compared to less than two minutes overall. This result may be helpful in requests for more equipment, more personnel, or justifying another fire station.

As an example of improved resource allocation, statistical analysis of emergency medical calls can determine the impact of providing another paramedic unit in the field. Increasing the number of EMS units from four to five may, for example, decrease average response times from five minutes to three minutes – a change that may save lives.

Another reason for analysis is to identify training needs. Most training on fire fighting is based on a curriculum that has been in place for many years. It makes sense to see how training matches characteristics of fires in a particular jurisdiction. This is not to say that other training is not important, since an exception can always occur. However, knowing more about the fires in an area can improve the training. Additionally, an analysis of fire fighter injuries may indicate a need for certain types of training.

National Fire Incident Reporting System (NFIRS)

The National Fire Incident Reporting System (NFIRS) began over 25 years ago with the aim of collecting and analyzing data on fires from departments across the country. More than 14,000 fire departments in 42 states now report their fires and injuries to NFIRS. This makes NFIRS the largest collector of fire-related incident data in the world. NFIRS contributes over 900,000 fire incidents each year to the National Fire Database.

Incident data collection is not new. In 1963 the National Fire Protection Association (NFPA) developed a dictionary of fire terminology and associated numerical codes to encourage fire departments to use a common set of definitions. This dictionary is known as the NFPA 901, Standard Classifications for Incident Reporting and Fire Protection Data. The current set of codes used in NFIRS version 5.0 represents the merging of the ideas from NFPA 901 and the many suggested improvements from the users of the NFIRS 4.1 coding system.

Version 5.0 of NFIRS consists of 11 separate modules in which fire departments can report any type of incident they respond to. The basic module (Module 1), which is required, includes incident number and type, date, day of the week, alarm time, arrival time, time in service, and type of action taken. Modules 2 through 5 are required if applicable. If the incident is a fire, the fire module (Module 2) is completed. This includes property details, cause of ignition, human factors, equipment involved, and other information. If it is a structure fire, Module 3 is completed. This would include such things as structure type, main floor size, fire origin, presence of detectors and automatic extinguishment equipment, and other data. If there were civilian casualties or fire service casualties, Modules 4 or 5, respectively, would be filled out. The remaining modules are optional at the local level. They include EMS (Module 6), Hazardous Material (Module 7), Wildland Fire (Module 8), Apparatus or Resources (Module 9), Personnel (Module 10), and Arson (Module 11).

Usually, the state fire marshal’s office in each NFIRS state has the responsibility for collecting data from its fire departments. They normally collect data in two ways. One way is that fire departments without any data processing capabilities send their paper reports to the fire marshal’s office. The State Fire Marshal’s Office then enters the reports into a computer system.

Local departments with data processing capabilities send their data electronically or on diskettes or tapes. In either case, the state fire marshal’s office merges all reports onto a database.

This statewide database then is forwarded electronically to the National Fire Data Center (NFDC) at the U.S. Fire Administration (USFA). The NFDC then can compare and contrast statistics from states and large metropolitan departments to develop national public education campaigns, make recommendations for national codes and standards, guide allocations of federal funds, ascertain consumer product failures, identify the focus for research efforts, and support federal legislation.

Every fire department is responsible for managing its operations in such a way that fire fighters can do the most effective job of fire control and fire prevention in the safest way possible. Effective performance requires careful planning, which can take place only if accurate information about fires and other incidents is available. Patterns that emerge from the analysis of incident data can help departments focus on current problems, predict future problems in their communities, and measure their programs’ successes.

The same principle is applicable at the state and national levels. NFIRS provides a mechanism for analyzing incident data at each level to help meet fire protection management and planning needs. In addition, NFIRS information is used by labor organizations on a variety of matters, such as workloads and fire-fighter injuries.

References

• FEMA. (2004). Fire Data Analysis Handbook, Second Edition. (p. 1-4). Also available at http://www.usfa.fema.gov/downloads/pdf/publications/fa-266.pdf as of December 27, 2012.

2-2:  USFA Civilian Fire Fatality Reports

Findings

Ninety-two percent of all civilian fire fatalities in residential buildings suffered from thermal burns and smoke inhalation.

Bedrooms (53 percent) were the leading specific location where civilian fire fatalities occurred in residential buildings.

Fifty-one percent of civilian fire fatalities in residential buildings occurred between the hours of 11 p.m. and 7 a.m. This period also accounted for 48 percent of fatal fires in residential buildings.

Thirty-six percent of fire victims in residential buildings were trying to escape at the time of their deaths; an additional 35 percent were sleeping.

“Other unintentional, careless” actions (16 percent) and “smoking” (15 percent) were the leading causes of fatal fires in residential buildings.

Males accounted for 57 percent of civilian fire fatalities in residential buildings; females accounted for 43 percent of the fatalities.

Forty-five percent of civilian fatalities in residential building fires were between the ages of 40 and 69.

Thirteen percent of civilian fire fatalities in residential buildings were less than 10 years old.

Fires can strike anywhere — in structures, buildings, automobiles and the outdoors. Fires that affect our homes are often the most tragic and the most preventable. It is a sad fact, but each year over 75 percent of all civilian fatalities occurred as a result of fires in residential buildings — our homes. Between 2009 and 2011, civilian fire fatalities in residential buildings accounted for 82 percent of all fire fatalities. This topical fire report focuses on the characteristics of these fatalities.

Civilian fire fatalities by definition involve people not on active duty with a firefighting organization who die as a result of a fire. These fatalities generally occur when an individual is escaping, sleeping, or is unable to act during a fire.

Annually from 2009 to 2011, an estimated 2,495 civilian fire fatalities resulted from 1,600 fatal fires in residential buildings and an estimated 360,900 residential building fires. Fatal fires are those fires where one or more fatalities occur.

As previously noted, this report focuses on the characteristics of civilian fire fatalities (e.g., gender, race and age of the victim, activity prior to death, etc.) in residential buildings as opposed to the characteristics of the fires (e.g., fire spread, factors contributing to ignition, alerting/suppression systems, etc.) from which these fatalities occurred. The characteristics of these fires are discussed in a separate topical fire report titled, “Fatal Fires in Residential Buildings (2009-2011),” Volume 14, Issue 3, May 2013.

The National Fire Incident Reporting System data are used for the analyses presented throughout the report. For the purpose of this report, the term “residential building fires” is synonymous with “residential fires.” “Residential fires” is used throughout the body of this report; the findings, tables, charts, headings and endnotes reflect the full category “fires in residential buildings” or “residential building fires.”

Civilian Fire Fatality Rates in Residential Buildings

Not all fires produced fatalities. When civilian fatalities were averaged across all residential fires, the overall fatality rate was nearly 6 civilian fatalities per 1,000 residential fires (Table 1). Residential fires that resulted in fatalities had 1,214 fatalities for every 1,000 fires or slightly more than one fatality per fatal fire. Of the residential fatal fires, 86 percent resulted in one civilian fatality, 10 percent resulted in two civilian fatalities, and 4 percent resulted in three or more civilian fatalities.

Table 1. Fatality Rates for Residential Building Fires per 1,000 Fires (2009–2011)

| Fatalities per 1,000 Fatal Fires | Fatalities per 1,000 Residential Building Fires |
| --- | --- |
| 1,213.6 | 5.5 |

When Fatal Fires in Residential Buildings Occur

As shown in Figure 1, residential fatal fires occurred most frequently late at night or in the very early morning when most people were sleeping, a major factor contributing to the fatality (see Table 2). From 2009 to 2011, fatal fires were highest between 1 to 2 a.m. and 4 to 5 a.m. Fatal fires were most prevalent when overall residential fire incidence was at its lowest, making nighttime fires the most deadly. The 8-hour peak period (11 p.m. to 7 a.m.) accounted for 48 percent of residential fatal fires and 51 percent of fatalities.

Factors Contributing to Civilian Fire Fatalities in Residential Buildings

The most notable factors contributing to the fatalities (outside of “other (unspecified) factors”) (Figure 3) were “fire pattern” (61 percent), “egress problems” (17 percent) and “escape problems” (16 percent). Fire pattern factors involve situations where exits are blocked by smoke and flame, vision is blocked or impaired by smoke, and civilians are trapped above or below the fire. Egress problems include such factors as crowded situations, limited exits, locked exits or other exit problems, and mechanical obstacles to the exit. Escape factors include unfamiliarity with exits, excessive travel distance to the nearest clear exit, choice of an inappropriate exit route, re-entering the building, and clothing catching on fire while escaping.

Figure 3

Human Factors Contributing to Civilian Fire Fatalities

Human factors played an important role in residential fire fatalities. The leading human factor contributing to fatalities was being “asleep” (45 percent). This finding was not unexpected as the largest numbers of fatalities occurred between 11 p.m. to 7 a.m. “Physical disability” was the second leading human factor contributing to fatalities (27 percent). This was followed by “possibly impaired by alcohol” and “unconscious” at 20 percent and 9 percent, respectively.

Primary Symptoms of Civilian Fire Fatalities

Ninety-two percent of all fatalities in residential fires suffered from thermal burns and smoke inhalation. Burns and smoke inhalation combined made up 47 percent of the fatalities. Smoke inhalation by itself accounted for 39 percent of residential fire fatalities and thermal burns (as opposed to scalds or chemical or electrical burns) alone accounted for 5 percent of fatalities (Figure 4).8 Cardiac arrests accounted for only 3 percent of fatalities. Thermal burns are caused by contact with flames, hot liquids, hot surfaces and other sources of high heat. Eighty-four percent of thermal burn fatalities were the result of thermal burns on multiple body parts. Smoke inhalation affects the internal organs, specifically the lungs and airways within the body. It results from breathing smoke that contains harmful gases and small particles that are present in the air during a fire. These gases and particles include chemicals or toxins which can lead to inflammation and blockage of the airway.

Causes of Fatal Fires in Residential Buildings

“Other unintentional, careless” actions (16 percent) and “smoking” (15 percent) were the leading causes of residential fires that resulted in fatalities — fatal fires.10 These two fire causes accounted for 31 percent of all residential fatal fires. “Other unintentional, careless” actions include misuse of materials or products, abandoned or discarded materials or products, and heat source too close to combustibles. The next leading cause, “electrical malfunction,” accounted for an additional 11 percent of residential fatal fires as shown in Figure 5.11 The cause of the fire was “unknown” in 46 percent of fatal fires.

Civilian Activity Prior to Death

Most civilian fire fatalities occurred when the victim was attempting to escape (36 percent) or sleeping (35 percent) as shown in Figure 6. To escape a fire, many civilians make the mistake of fleeing through the area where the fire is located. The area of a fire has tremendous heat, smoke, and a toxic atmosphere that can render a person unconscious. As a result, it is imperative that an escape plan be prepared and practiced. With a well-thought-out plan and multiple escape options, the chances of survival and escaping greatly increase. In addition, it has been proven that people cannot wake up from the smell of fire while sleeping. Therefore, it is also vital that smoke alarms are installed in homes to alert sleeping people to the presence of fire.

Gender, Race and Ethnicity of Civilian Fire Fatalities

Males accounted for 57 percent of residential fire fatalities; females accounted for 43 percent of fire fatalities. Where racial information was provided, whites constituted 68 percent of the fatalities followed by blacks or African-Americans (26 percent). All other races accounted for 6 percent of fire fatalities (Figure 7). Race was not specified for 37 percent of the fatalities. Where ethnicity data were provided, 91 percent of civilian fatalities were non-Hispanic or non-Latino. The remaining 9 percent were Hispanic or Latino. Ethnicity was not specified for 57 percent of the fatalities.

Age and Activity Prior to Death

Forty-five percent of civilian fatalities in residential fires were between the ages of 40 and 69 (Figure 8). Thirteen percent of fatalities were less than 10 years old. Adults age 70 and over accounted for 24 percent of fatalities.

Where the information was reported, at the time of death, escaping (36 percent) and sleeping (35 percent) were the two leading activities that resulted in fatalities. Children aged 0 to 9 were primarily sleeping (48 percent) over trying to escape (26 percent). Those aged 10 to 49 were also more likely to be sleeping at the time of their deaths. Those aged 50 and over were more likely trying to escape at the time of their deaths as opposed to sleeping (Table 3). Overall, activity at the time of the fatal injury was reported for 34 percent of the fatalities.

Specific Location of Fire Fatality

Bedrooms (53 percent) were the leading specific location where civilian fire fatalities occurred in residential buildings. Common rooms such as dens, family rooms, living rooms, or lounges (9 percent); bathrooms and lavatories (8 percent); other functional areas (7 percent); and kitchens and cooking areas (5 percent) accounted for an additional 29 percent. While not specific rooms in the home, egress areas accounted for 10 percent of fatalities. Exits such as corridors, stairways and doors can get filled with smoke, fire, or extreme heat, making escape routes treacherous.

Examples

The following recent examples illustrate fire scenarios in which civilian fatalities have occurred:

January 2013: A 78-year-old man died in an early morning house fire in South Roxana, Ill. When firefighters arrived on scene of the two-alarm fire, they found a fully involved structure fire. After the flames were put out, the victim, who lived alone, was found in the back part of the house and in the area of a wood stove. The man reportedly may have been using the wood stove to help heat the home.

January 2013: Investigators with the Kentucky State Fire Marshal’s Office believe that a space heater that was too close to combustible materials in the living room started a Pike County, Ky., house fire that killed a 39-year-old father and his four children whose ages ranged from 6 months to 5 years. All five victims were found on the mattress pad they were sleeping on in the living room. The children’s mother was able to make it out of the house but was admitted to the hospital for treatment of severe burns. The home reportedly did not have working smoke alarms.

January 2013: Rockdale County officials determined that a boy playing with a lighter started a Conyers, Ga., duplex fire that killed four of his siblings and left his mother badly burned. The fire started near a second-floor bathroom, and the home had one non-working smoke alarm on the first floor. The ages of the four children who died ranged from 8 months to 9 years. The 6-year-old boy who started the fire survived after being thrown by his mother from a second-story window. A grandmother was also inside the house at the time of the fire but survived.

January 2013: A mother, 52, and daughter, 28, died following an early morning house fire on the north side of Akron, Ohio. Firefighters made an aggressive attack to quickly extinguish the blaze and found the two victims in the bedrooms of the home. While the cause was being investigated, it was determined that the fire started on the first floor of the home and spread to the basement and the second floor. In addition, no working smoke alarms were found inside the home. Damages to the home were estimated at $40,000 with an additional $20,000 in contents.

Escape Planning for Residential Buildings

Everyone should know how to escape from his or her residence. The U.S. Fire Administration recommends leaving fighting a fire to trained firefighters. Instead, efforts should be focused on following a preset escape plan.

A home filled with smoke is a very dangerous situation. Smoke blocks vision, and the toxic gases can cause dizziness, disorientation and ultimately death. Under these conditions, one can easily become lost or trapped in the home. Unfamiliarity with exits, excessive distance to the nearest exit, or an inappropriate choice of exit can hinder a crucial escape. Many civilian fatalities occur as the victim is trying to escape. With a well-thought-out plan and multiple escape options, your chances of survival greatly increase.

The first step in an escape plan is to make sure smoke alarms are installed on every level of the home and are in good working order. Plan and practice at least two escape routes for every room and have procedures in place for those who require additional help such as infants, older adults and individuals with disabilities. For more information on preparing and practicing a fire escape plan, visit http://www.usfa.fema.gov/campaigns/smokealarms/escapeplans/index.shtm.

3-2 Pre-Incident Plans

Pre-incident Plan Symbols and Documents

Pre-incident plan diagrams should use standardized symbols to represent building construction, fire protection system, and hazard data.

Preplan Symbols

Preplan symbols are adopted by the local agency. They are usually based on regional or national standards. Symbols are usually included for:

• Building Construction

• Water Supply and Distribution

• Utility and HVAC Controls

• Egress and Access

• Fire Protection Systems

Pre-incident Plan Documents

A pre-incident plan contains general and detailed information that is used by responders to manage emergencies. The plan’s format is adopted by each local agency and usually consists of an information summary form and diagram.

Information Summary Form

Some agencies us summary forms for more detailed preincident data. Provide information related to the construction, physical layout, water supply, protection systems, utilities, hazards and other information of a building or facility. Additional data can include fire flow, tactics, operations of HVAC systems, etc.

Building Diagrams

Presents preplan information in a clear, concise and visual format. Details of diagrams vary by agency. Diagrams can be plot plans of building and facility layouts and more detailed floor plans of specific buildings. Information relevant for emergency operations should be included. Other planning information should be included on a summary form.

Diagram Examples

Diagram format varies by agency. These are examples of a plot plan and floor plan used by a local California agency.

References

• NFPA 170: Standard for Fire Safety and Emergency Symbols, Sections XXX

• NFPA 1620: Standard for Preincident Planning, Sections 1.1, 3.3.41, 4.6, A4.6, and p. 191-194.

4-6 Follow Up Procedures

Code Enforcement and Appeal Process

The Role of the Company Officer in Regards to Code Enforcement

Is a “reasonable degree of fire safety” a subjective judgment made by inspectors? It can be argued that most codes and standards were developed based upon a previous large fire loss or fire fatality. Lessons learned from fires such as the Iroquois Theater Fire, Shirtwaist Fire, and the Beverly Hills Supper Club helped redefine fire codes and standards, as we know them.

Codes and Fire Hazards

Adopted codes, standards, and ordinances are generally adopted to address past issues in fire loss history. As such, a reasonable degree of fire safety is attained by general compliance with codes. However, we live in a time of ever-changing technologies and conditions. There will always be instances where codes and standards do not address the situations at hand. In these cases, the inspector must rely on the factual conditions presented, coupled with a sound understanding of fire behavior, chemistry, and physics. Only then can the spirit of the code, fire prevention in particular, be achieved.

The NFPA 550 Guide to the Fire Safety Concept Tree introduces a concept model that achieves reasonable fire safety by addressing the objectives of preventing fire ignition or managing fire impact.

Given the basic knowledge of the fire tetrahedron, we can apply the first of these two objectives by preventing fire ignition with separation or control. Providing separation or control of ignition sources will ensure that heat does not mix with oxygen and fuels to begin the combustion process. Required fire-rated walls with automatic door closures are a common example utilized to separate boilers or incinerators from storage areas.

The second objective acknowledges that we will not prevent every fire that occurs. With this in mind, we must mitigate or lessen the negative effects of fire after a fire occurs. Understanding the various stages of fire and trying to shape positive reactions prior to free burning or flashover may be enough to ensure early extinguishment or evacuation from a building. Automatic fire sprinklers have an outstanding track record in controlling fires at early stages and preventing flashover. Automatic heat or smoke detectors can identify products of combustion early to begin an evacuation plan.

The advantages of a sound company inspection program are clear. Company Officers should recognize the role their presence plays in fire prevention and address the "big ticket" items they find that will prevent fire or reduce the damage from fire. Where time does not permit or the issues are beyond the knowledge of company personnel, these issues should be brought to the attention of the Fire Prevention Bureau.

Obvious issues are:

• Sources of ignition

• Fuel loads

• Exiting issues

The fire company inspection is also a pre-fire opportunity to ensure location and reliability of tactical issues such as:

• Fire apparatus access

• Fire protection equipment

• Entry and egress points

Violations

Determining the "severity" of a violation will help the Company Officer achieve a reasonable degree of fire safety. This will allow the Company Officer to make determinations about correction or mitigation options.

Routine hazards are the most frequent of hazards and violations found. While the hazard or violation is not code compliant, the condition itself would not be the immediate cause of a fire or unsafe condition. For instance, the use of electrical extensions cords, fire extinguishers that are past due for service, etc.

Imminent hazards occur when it becomes obvious that the hazard or process poses an immediate hazard to life and property. Examples include blocked exits, inoperable fire alarm systems, or open flames or heat sources adjacent to combustibles.

Transient hazards are specific occurrences, which should be acted upon immediately through a citation. Changeable violations are corrected by the person responsible on a temporary basis (in most cases), but are changed back after the inspector leaves the premises. The same situations may be encountered annually and are not under continuous abatement. Examples include Christmas tree lots or overstocked storage areas during the holiday season.

Regardless of the hazards or violation types, communications should be made to the responsible person(s) to ensure each item is addressed. While it may be acceptable for a reasonable amount of time to be given for the correction of routine hazards or transient hazards, imminent hazards should be corrected or mitigated prior to the inspector leaving the premises.

Compliance

A sound inspection program should always seek to attain compliance at the lowest level. Prior to completing the inspection, the Company Officer should ensure the building has a reasonable degree of fire safety and will make appropriate modifications or corrections to ensure fire safety for all persons, including first responders.

Voluntary compliance consists of:

• Education

• Partnering

• Bargaining legal compliance:

o Administrative citation

o Notice and order

o Misdemeanor

o Abatement order

The Code Enforcement Appeal Process

As with all enforcement proceedings, there is an appeal process to code enforcement procedures. This process may vary based upon the jurisdiction you come from. Most jurisdictions start with an informal process for appeal whereas person(s) may appeal the

decision of the inspector or Company Officer through the fire department’s hierarchy. Individuals should check with their respective fire department’s policies or procedures to identify their department’s expectations. An example of an appeal process is shown in your text (Figure 4.6, Page 60 of Fire Prevention Applications for the Company Officer).

Fire Code Board of Appeals

The International Fire Code appeal process recognizes the use of a Board of Appeals. While a fire code official is an ex-officio member of the board, the official does not have a vote on any matter the goes before the board. The Board of Appeals may order to hear and decide appeals of orders, decisions, or determinations bade by the Company Officer relative to the application and interpretation of the fire code. All decisions and findings shall be made in writing to the appellant.

In lieu of a fire code appeals board, a jurisdiction may opt to pre-designate an appeal-hearing officer with the same responsibilities as a Fire Code Board of Appeals.

Interpretations of State Fire Marshal Regulations

Any person may request an interpretation of regulation(s) adopted by the state fire marshal. The state fire marshal shall review the issue with the appropriate local enforcement agency prior to rendering an interpretation.

Appeal of Alternate Means of Protection in State Regulated Occupancies

If a jurisdiction denies a request for an alternate means of protection in a state regulated occupancy, an applicant may appeal directly to the state fire marshal for consideration. The state fire marshal may seek the advice of the State Board of Fire Services. Upon considering the facts presented, including any recommendations of the State Board of Fire Services, the state fire marshal shall render a decision and transmit the findings and any recommendations back to the applicant and to the enforcing agency.

References

• NFPA 550 Guide to the Fire Safety Concept Tree, NFPA 2007 Edition.

• (2010) California Fire Code. California Building Standards Commission. (§1.11.2.1.2, §1.11.25).

5-1 Hazard0us Processes

Fuel Dispensing Operations

General Fuel-dispensing Definitions

Aircraft Motor Vehicle Fuel-dispensing Facility: That portion of property where flammable or combustible liquids or gases used as motor fuels are stored and dispensed from fixed automotive-type equipment into the fuel tanks of aircraft.

Automotive Motor Fuel-dispensing Facility: That portion of property where flammable or combustible liquids or gases used as motor fuels are stored and dispensed from fixed equipment into the fuel tanks of motor vehicles.

Marine Motor Fuel-dispensing Facility:   That portion of property where flammable or combustible liquids or gases used as fuel for watercraft are stored and dispensed from fixed equipment on shore, piers, wharves, floats or barges into the fuel tanks of watercraft.

Self-Service Motor Fuel-dispensing Facility: That portion of motor fuel-dispensing facility where liquid motor fuels are dispensed from fixed approved dispensing equipment into the fuel tanks of motor vehicles by persons other than a motor fuel-dispensing facility attendant.

Motor Fuel Dispensing Facility Requirements

Emergency disconnect switches:

An approved, clearly identified and readily accessible emergency disconnect switch shall be provided at an approved location to stop the transfer of fuel to the fuel dispensers in the event of a fuel spill or other emergency. An emergency disconnect switch for exterior fuel dispensers shall be located within 100 feet of, but not less than 20 feet from the fuel dispensers.

Attended Self-service Motor Fuel-dispensing Facilities:

Attended self-service motor fuel-dispensing facilities shall comply with Sections 2204.2.1 through 2204.2.5. Attended self-service motor fuel-dispensing facilities shall have at least one qualified attendant on duty while the facility is open for business. The attendant's primary function shall be to supervise, observe and control the dispensing of fuel. The attendant shall prevent the dispensing of fuel into containers that do not comply with Section 2204.4.1, control sources of ignition, give immediate attention to accidental spills or releases, and be prepared to use fire extinguishers. Ref: CFC, 2010 Edition, Section 2204.2, page 302

Unattended Self-service Motor Fuel-dispensing Facilities:

Where approved, unattended self-service motor fuel-dispensing facilities are allowed. As a condition of approval, the owner or operator shall provide, and be accountable for, daily site visits, regular equipment inspection and maintenance.

Sources of Ignition:

Smoking and open flames shall be prohibited in areas where fuel is dispensed. The engines of vehicles being fueled shall be shut off during fueling.

Warning signs:

Shall be conspicuously posted within sight of each dispenser in the fuel-dispensing area stating:

• No smoking

• Shut off motor

• Discharge your static electricity before fueling by touching a metal surface away from the nozzle

• To prevent static charge, do not reenter your vehicle while gasoline is pumping

• If a fire starts, do not remove nozzle-back away immediately

• It is unlawful and dangerous to dispense gasoline into unapproved containers

• No filling of portable containers in or on a motor vehicle.

Place container on ground before filling

Portable Fire Extinguishers

An approved portable fire extinguishers with a minimum rating of 2-A:20-B:C shall be provided and located not more than 75 feet from pumps, dispensers or storage tank fill-pipe openings.

Housekeeping

Weeds, grass, brush, trash, and other combustible materials shall be kept not less than 10 feet from fuel-dispensing equipment.

Physical Protection of Aboveground Tanks

Guard posts shall be provided to protect above-ground tanks against impact by a motor vehicle unless the tank is listed as a protected above-ground tank with vehicle impact protection.

Dispenser Hose

Dispenser hoses shall be a maximum of 18 feet in length unless otherwise approved.

Gravity and Pressure Dispensing

Flammable liquids shall not be dispensed by gravity from tanks, drums, barrels or similar containers. Flammable or combustible liquids shall not be dispensed by a device operating through pressure within a storage tank, drum or container.

Liquefied Petroleum Gas Motor Fuel Dispensing Facilities

Hoses

Hoses and piping for the dispensing of LP-gas shall be provided with hydrostatic relief valves. The hose length shall not exceed 18 feet, an approved method shall be provided to protect the hose against mechanical damage.

Vehicle Impact Protection

Vehicle impact protection for LP-gas storage containers, pumps and dispensers shall be provided.

Compressed Natural Gas (CNG) Motor Fuel Dispensing Facilities

Location of Dispensing Operations and Equipment

Compression, storage and dispensing equipment shall be located above ground and outside unless approved by the California Building Code. Dispensing equipment shall be installed as follows:

• Not beneath power lines

• Ten feet or more from the nearest building or lot line that could be built on:

o Public street

o Sidewalk

o Source of ignition

• Fifty feet or more from the vertical plane below the nearest overhead wire of a trolley bus line

Emergency Shutdown Control

An emergency shutdown control shall be located within 75 feet of, but not less than 25 feet from, dispensers and shall also be provided in the compressor area.

Grounding and Bonding

The structure or appurtenance used for supporting the cylinder shall be grounded in accordance with the California Electrical Code.

Signage

Approved "No Smoking" signs shall be posted within 10 feet of the cylinder support structure or appurtenance, and Approved “CYLINDER SHALL BE BONDED” signs shall be posted on the cylinder support structure or appurtenance.

Hydrogen Motor Fuel Dispensing & Generation Facilities

Listed Equipment

Hoses, hose connections, compressors, hydrogen generators, dispensers, detection systems and electrical equipment used for hydrogen shall be listed for use with hydrogen. Hydrogen motor fueling connections shall be listed and labeled for use with hydrogen.

Maintenance

Gaseous hydrogen systems and detection devices shall be maintained in accordance with the manufacturer's instructions.

Smoking

Smoking shall be prohibited in hydrogen cutoff rooms. "No Smoking" signs shall be provided at all entrances to hydrogen cutoff rooms.

Ignition Source Control

Open flames, flame-producing devices and other sources of ignition shall be controlled at all times.

Housekeeping

Hydrogen cutoff rooms shall be kept free from combustible debris and storage at all times.

Fire Extinguishing Systems

Fuel-dispensing areas under canopies shall be equipped throughout with an approved automatic sprinkler system.

Protection from Vehicles

Guard posts or other approved means shall be provided to protect hydrogen storage systems and use areas subject to vehicular damage.

Marine Motor Fuel Dispensing Facilities

Dispensing

Wharves, piers or floats at marine motor fuel-dispensing facilities shall be used exclusively for the dispensing or transfer of petroleum products to or from marine craft is allowed.

Hoses and Nozzles

Dispensing of Class I, II or IIIA liquids into the fuel tanks of marine craft shall be by means of an approved-type hose equipped with a listed automatic-closing nozzle without a latch-open device. Hoses used for dispensing or transferring Class I, II or IIIA liquids, when not in use, shall be reeled, racked or otherwise protected from mechanical damage.

Housekeeping

Marine motor fuel-dispensing facilities shall be maintained in a neat and orderly manner.

Spills

Spills of Class I, II or IIIA liquids at or on the water shall be reported immediately to the fire department and jurisdictional authorities.

Rubbish Containers

Metal containers with tight-fitting or self-closing metal lids shall be provided for the temporary storage of combustible trash or rubbish.

Smoking

Smoking or open flames shall be prohibited within 50 feet of fueling operations. "No Smoking" signs shall be posted conspicuously about the premises.

Warning Signage

Warning signs shall be prominently displayed at the face of each wharf, pier or float at such elevation as to be clearly visible from the decks of marine craft being fueled. Such signs shall have letters not less than 3 inches in height on a background of contrasting color bearing the following or approved equivalent wording:

WARNING

NO SMOKING-STOP ENGINE WHILE FUELING,

SHUT OFF ELECTRICITY.

DO NOT START ENGINE UNTIL AFTER BELOW

DECK SPACES ARE VENTILATED.

Standpipe Hose Stations

Fire hose, where provided, shall be enclosed within a cabinet, and hose stations shall be labeled:

FIRE HOSE

EMERGENCY USE ONLY

Obstruction of Fire Protection Equipment

Materials shall not be placed on a pier in such a manner as to obstruct access to fire-fighting equipment or piping system control valves.

Portable Fire Extinguishers

Portable fire extinguishers having a minimum rating of 20-B: C, shall be provided as follows:

• One on each float

• One on the pier or wharf within 25 feet of the head of the gangway to the float

Unless the office is within 25-feet of the gangway or is on the float and an extinguisher is provided thereon

High-piled Storage

California Fire Code Definition

Combustible materials in closely packed piles more than 12 feet high. Height is measured from the floor to the top of the storage, not to the top of the shelf. Combustible materials on pallets or in racks more than 12 feet high. Special hazard commodities over 6 feet high, including tires, plastics and flammable liquids.

Housekeeping and Maintenance

To maintain high-piled storage, one must maintain the structural integrity of the racks. Smoking is prohibited, and an approved sign must be posted. Aisles must be kept clear of storage and waste materials.

Fire Protection and Life Safety System Requirements

Fire Protection and Life Safety Systems and Features depend on

• Size of building

• Type of commodity

• Height of racks

These systems may include

• Building sprinklers

• In-rack sprinklers

• Heat and smoke detectors

• Hose cabinets

• Fire extinguishers

• Smoke removal system

Building Access

Roadways shall be provided to within 150 feet of all portions of the building; access doors must be readily accessible and one or more access doors shall be provided in each 100 linear feet of exterior wall.

Tire Storage

Outdoor Storage

Tire storage is restricted to 5,000 square feet per pile with a maximum height of 10 feet height. Tire storage piles must be separated from other tire piles, combustible vegetation and products by 40 feet and from buildings and property lines by 50 feet (12 192 mm).

Inside Storage

Where tires are stored on-tread, the dimension of the pile in the direction of the wheel hole shall not be more than 50 feet. Tires stored adjacent to or along one wall shall not extend more than 25 feet from that wall. Other piles shall not be more than 50 feet.

Fire Department Access

New and existing tire storage yards shall be provided with fire apparatus access roads so that all points of the storage area are within 150 feet of the road. Fire apparatus access roads shall be located at least 20 feet from storage piles.

Tents and Membrane Structures

An Operational Permit is required for air supported temporary membrane structures, tents and canopies with an area greater than 200 square feet or a canopy over 400 square feet. Permits are not required for recreational camping tents or fabric canopies that are open on all sides and which comply with all of the following:

• Individual canopies having a maximum size of 700 square feet.

• The aggregate area of multiple canopies placed side by side, without a minimum firebreak of 12 feet, does not exceed 700 square feet.

• A minimum clearance of 12 feet to structures and other tents shall be provided.

Temporary tents, air-supported, air-inflated or tensioned membrane structures and canopies shall not be erected for a period of more than 180 days per year at one location.

Exits

Exits shall be provided and clearly marked. Exit signs shall be installed at all required exits and must clearly indicate the direction of egress travel when the exit serves an occupant load of 50

or more. Exit signs must be an approved self-luminous type or shall be internally or externally lit. The required width of exits, aisles and passageways shall be maintained at all times to a public way.

Combustible Materials

Hay, straw, shavings or similar combustible materials shall not be located within any tent, canopy or membrane structure containing an assembly occupancy except for that which is necessary for feeding and care of animals.

Sawdust and shavings utilized for a public performance or exhibit shall not be prohibited and the sawdust and shavings must be kept damp. Combustible materials shall not be permitted under stands or seats at any time and trash shall be removed at least once a day.

The areas within and adjacent to the tent or air-supported structure shall be maintained clear of all combustible materials or vegetation within 20 feet of the structure.

Heating and Cooking Equipment

The Fire Code permits food warming, cooking demonstrations and similar operations using

solid flammable fuel, butane or other similar devices that do not pose an ignition hazard.

Cooking tents must be separated from other tents, canopies or membrane structures by a minimum of 20 feet. Outdoor cooking that produces sparks or grease-laden vapors shall not be performed within 20 feet of a tent, canopy or membrane structure.

LP-gas equipment such as tanks, piping, hoses, fittings, valves, tubing and other related components must be approved. LP-gas containers shall be located outside of tent. Portable LP-gas containers with a capacity of 500 gallons or less shall have a minimum separation between the container and structure of not less than 10 feet.

5-2 Hazardous Materials

Definitions

Control Area: Spaces within a building where quantities of hazardous materials not exceeding the maximum allowable quantities (MAQ’s) per control area are stored, dispensed, used or handled (refer to Maximum Allowable Quantities).

Dispensing:  The pouring or transferring of any material from a container, tank or similar vessel, whereby vapors, dusts, fumes, mists or gases are liberated to the atmosphere.

Flammable Vapors or Fumes: The concentration of flammable constituents in air that exceeds 25% of their lower flammable limit (LFL).

Health Hazards: Materials with a primary classification as a health hazard can also pose a physical hazard, i.e., highly toxic and toxic materials, and corrosive materials. Hazardous materials shall be classified according to hazard categories. The categories include materials regulated by Chapter 27 and materials regulated elsewhere in the California Fire Code.

Immediately Dangerous To Life And Health (IDLH): The concentration of airborne contaminants that poses a threat of death, immediate or delayed permanent adverse health effects, or effects that could prevent escape from such an environment. This contaminant concentration level is established by the National Institute of Occupational Safety and Health (NIOSH) based on both toxicity and flammability.

Incompatible Materials: Materials that, when mixed, have the potential to react in a manner which generate heat, fumes, gases or byproducts which are hazardous to life or property.

Maximum Allowable Quantity (MAQs) Per Control Area:  The maximum amount of a hazardous material allowed to be stored or used within a control area inside a building or an outdoor control area. The MAQ per control area is based on the material state (solid, liquid or gas) and the material storage or use conditions.

Mixtures:  Mixtures shall be classified in accordance with hazards of the mixture as a whole. Mixtures of hazardous materials shall be classified in accordance with nationally recognized reference standards; by an approved qualified organization, individual, or Material Safety Data Sheet (MSDS); or by other approved methods.

Normal Temperature and Pressure (NTP): A temperature of 70°F (21°C) and a pressure of 1 atmosphere [14.7 psia (101 kPa)].

Physical Hazard: A material with a primary classification as a physical hazard can also pose a health hazard, i.e., explosives and blasting agents, combustible liquids, flammable solids, liquids and gases, organic peroxide solids or liquids, oxidizers, solids or liquids, oxidizing gases, pyrophoric solids, liquids or gases, unstable (reactive) solids, liquids or gases, water-reactive solids or liquids, cryogenic fluids.

Safety Can: An approved container of not more than 5-gallon (19 L) capacity having a spring-closing lid and spout cover so designed that it will relieve internal pressure when subjected to fire exposure.

Use (Material): Placing a material into action, including solids, liquids and gases.

General Requirements

Defective Containers and Tanks

Defective containers and tanks shall be removed from service, repaired in accordance with approved standards or disposed of in an approved manner.

Unauthorized Discharge

When hazardous materials are released in quantities reportable under state, federal or local regulations, the fire code official shall be notified.

Records

Accurate records shall be kept of the unauthorized discharge of hazardous materials by the permit holder.

Responsibility for cleanup

The person, firm or corporation responsible for an unauthorized discharge shall institute and complete all actions necessary to remedy the effects of such unauthorized discharge, whether sudden or gradual, at no cost to the jurisdiction. When deemed necessary by the fire code official, cleanup may be initiated by the fire department or by an authorized individual or firm. Costs associated with such cleanup shall be borne by the owner, operator or other person responsible for the unauthorized discharge.

Material Safety Data Sheets (MSDS)

Material Safety Data Sheets (MSDS) shall be readily available on the premises for hazardous materials regulated by Chapter 27 of the California Fire Code. When a hazardous substance is developed in a laboratory, available information shall be documented.

Identifying Hazardous Materials

Hazard Identification Signs

Unless otherwise exempt by the fire code official, visible hazard identification signs as specified in NFPA 704 for the specific material contained shall be placed on stationary containers, aboveground tanks, and at entrances to locations where hazardous materials are stored, dispensed, used or handled in quantities requiring a permit and at specific entrances and locations designated by the fire code official.

Markings

Individual containers, cartons or packages shall be conspicuously marked or labeled in an approved manner.

Rooms or cabinets containing compressed gases shall be conspicuously labeled in capital letters: COMPRESSED GAS.

Signs and markings required by Sections 2703.5 and 2703.5.1of the California Fire Code shall not be obscured or removed, shall be in English as a primary language or in symbols allowed by this code, shall be durable, and the size, color and lettering shall be approved.

Transportation Placards, Labels, and Markings - UN Placarding System

The UN Placarding System provides uniform and standardized regulations for hazardous material identification. This enhances safety by improving capabilities for accurate recognition of hazardous materials or dangerous goods and by eliminating duplicate or inconsistent marking and labeling systems.

The UN Placarding System categorizes hazardous materials into nine classifications. These classify hazardous materials based on their actual and potential risks to people, property and the environment:

• Class 1: Explosives

• Class 2: Gases

• Class 3: Flammable liquids

• Class 4: Flammable solids, substances liable to ignite spontaneously, substances that  emit flammable gases on contact with water

• Class 5: Oxidizing substances and organic peroxides

• Class 6: Toxic and infectious substances

• Class 7: Radioactive substances

• Class 8: Corrosive substances

• Class 9: Miscellaneous dangerous substances and articles

The UN System uses four digit commodity identification numbers. Each hazardous material is assigned its own specific number. These numbers are displayed on placards, labels, orange panels, and/or white diamonds. They may also be found on orange panels, with the number preceded by the letters “UN.” UN product identification numbers are identified in yellow-bordered pages of Emergency Response Guidebook (ERG). These numbers should appear on shipping papers and should match numbers displayed on exteriors of tanks or shipping containers.

DOT Placards, Labels, and Markings

These systems are based on the UN system and classify hazardous materials according to primary dangers and assign standardized symbols to identify hazard classes and include additional categories such as “Other Regulated Materials” (ORM-Ds).

The standard U.S. system was developed by the Department of Transportation and uses placards, labels and markings.

A DOT placard is a diamond-shaped, color-coded sign that shippers provide to identify materials in transportation containers. Placards have regulations that specify their size, color, message, and visual graphics. They may be found on any container transporting any quantity of certain extremely hazardous materials and are required on any material shipped in quantities of 1,001 pounds (454 kg) or greater. Placards are not required when any of the materials listed in Table 14.11 is less than 1,001 pounds (454 kg) for any one shipment. They can be found on a bulk packages, rail tank cars, cargo tank vehicles, portable tanks, or unit loading devices containing hazardous materials over 640 cubic feet (18 m3) in capacity.

A DOT label is printed on 3.9-inch (100 mm) square-on-point diamond that may or may not have written text identifying the hazardous material inside the package. DOT labels communicate the hazards posed by the material if the package falls from the transport vehicle and spills its contents. Each hazard label class is assigned a pictogram and division number. The package will have a primary label for materials that meet definition of more than one hazard class. DOT labels provide information similar to vehicle placards and may be found on non-bulk packaging. Several DOT labels may be found side by side on packages with the primary hazard label located on left and secondary/subsidiary class label on right. Subsidiary classes must have class numbers displayed.

Improperly marked, unmarked, and otherwise illegal shipments are common. An inspector must be extremely suspicious of unmarked or mismarked containers.

OSHA Identification Marking Requirements

Other markings may not apply to all materials in transit. Some are required by the federal government for packages, containers, compartments, and buildings to indicate the presence of hazardous materials.

OSHA’s Hazardous Communications Standard (HCS) requires employers to identify hazards in workplace, train employees on hazard recognition, and ensure all hazardous material containers are labeled, tagged, or marked with the identity of the substances contained in them.

For OSHA identification marking requirements, chemical manufacturers and importers are required to provide appropriate labels on product containers that include the name of product, manufacturer’s contact information, precautionary hazard warnings, directions for use and handling, names of active ingredients, first aid instructions and other pertinent information.

NFPA 704 System

The NFPA 704 system provides a hazard number rating to rapidly identify the presence of hazardous materials and their potential severity based on health, flammability, instability, and other related hazards. It does not provide specific information on type, specific location, or quantity of material.

The 704 System is widely recognized method for indicating presence of hazardous materials. It is commonly required by local ordinances for all occupancies that contain hazardous materials. The 704 System is designed to alert emergency responders to health, flammability, instability, related hazards that may present short-term, acute exposures resulting from a fire, spill, or similar emergency. It is not designed for transportation, the general public use or for any of the following:

• Non-emergency occupational exposures

• Explosives and blasting agents

• Chronic health hazards

• Etiologic agents and other similar hazards

The 704 System uses the following design concepts:

• Ratings - uses system of numbers from 0 (minimal hazard) to 4 (severe hazard)

• Hazard Categories — Health, flammability, instability

• Hazard Categories are arranged on diamond-shaped marker or sign

o Health rating — Blue background

o Flammability hazard — Red background

o Instability — Yellow background

o Alternative Information — Background can be any contrasting color, with the number 0 to 4 represented by appropriate color.

• Special hazards are located in six o’clock position that has no specified background color (white is most common color used). Only three symbols presently authorized: o W — Indicates unusual reactivity with water

o OX — Indicates material is an oxidizer

o SA – “Simple Asphyxiants” (nitrogen, helium, neon, argon, krypton, xenon)

The NFPA 704 diamond does not identify the specific chemical (or chemicals) or the specific quantities present. Positive identification of materials needs to be made through other means such as container markings, employee information, company records or pre-incident surveys.

Manufacturer’s Labels and Warning Words

The U.S. Federal Hazardous Substances Act requires labels on products destined for use by consumer households to have one of the following signal words to indicate the degree of hazard associated with the product.

• Caution — May have minor health effects

• Warning — Moderate hazards that have significant health effects or flammability

• Danger — The highest degree of hazard; used on products that explode when exposed to heat

• Poison — Use in addition to danger on labels of highly toxic materials

General Hazardous Materials Issues

Industrial Trucks

Powered industrial trucks used in areas designated as hazardous (classified) locations in accordance with the California Electrical Code shall be listed and labeled for use in the environment intended in accordance with NFPA 505.

Hazardous Material in Group M and S: Display and Storage Areas

The aggregate quantity of nonflammable solid and nonflammable or noncombustible liquid hazardous materials allowed within a single control area of a Group M display and storage area or a Group S storage area is allowed to exceed the maximum allowable quantities per control area specified in Tables 2703.1.1(1) and 2703.1.1(2) in the California Fire Code without classifying the building or use as a Group H occupancy, provided that the materials are displayed and stored in accordance with Section 2703.11 of the California Fire Code.

Maximum Number of Cylinders Per Gas Cabinet

The number of cylinders contained in a single gas cabinet shall not exceed three.

Alcohol-based Hand Rub Dispensers

The use of wall-mounted dispensers containing alcohol-based hand rubs classified as Class I or II liquids shall be in accordance with all of the following:

• The maximum capacity of each dispenser shall be 68 ounces

• The minimum separation between dispensers shall be 48 inches

• The dispensers shall not be installed directly adjacent to, directly above or below an electrical receptacle, switch, appliance, device or other ignition source

• The wall space between the dispenser and the floor shall remain clear and unobstructed

• Dispensers shall be mounted so that the bottom of the dispenser is a minimum of 42 inches and a maximum of 48 inches above the finished floor

• Dispensers shall not release their contents except when the dispenser is manually activated

• Storage and use of alcohol-based hand rubs shall be in accordance with the applicable provisions of Sections 3404 and 3405

• Dispensers installed in occupancies with carpeted floors shall only be allowed in smoke compartments or fire areas equipped throughout with an approved automatic sprinkler system

Storage of Hazardous Materials

Secondary Containment for Hazardous Material Liquids and Solids

Where required by Table 2704.2.2 of the California Fire Code, buildings, rooms or areas used for the storage of hazardous materials liquids or solids shall be provided with secondary containment.

Monitoring

An approved monitoring method shall be provided to detect hazardous materials in the secondary containment system.

Containment Pallets

When used as an alternative to spill control and secondary containment for outdoor storage in accordance with the exception in Section 2704.2 of the California Fire Code, containment pallets shall comply with all of the following:

- A liquid tight sump accessible for visual inspection shall be provided

- The sump shall be designed to contain not less than 66 gallons (250 L)

- Exposed surfaces shall be compatible with material stored

- Containment pallets shall be protected to prevent collection of rainwater within the sump

Material Safety Data Sheet (MSDS)

Federal hazardous materials regulations have established “Employee Right to Know” laws. Employers must notify employees, and “visitors” (including first responders) about the known and potential hazards of all chemicals and other materials found in the workplace. Employers can comply with this regulation by permanently providing a readily available list of Hazardous Material Safety Data Sheets on the premises.

The California Fire Code requires employers to identify and maintain a list of all hazardous materials used in the workplace, including MSDS reference documents. These documents must

be updated on an as-needed basis. In addition, the employer is responsible for ensuring that all products are accurately labeled, provide a written hazardous materials mitigation plan and administer a training plan that teaches all employees about the chemical hazards found in their workplace. CAL-OSHA is primarily responsible for enforcing these requirements.

CAL-OSHA has established minimum formatting requirements for workplace MSDS documents. As applicable, each MSDS document will have eight sections of information provided for employee review and familiarization:

• Chemical Manufacturer's Information o Name and address

o Emergency telephone number

o Information telephone number

o Signature and data

• Hazardous ingredients o Common name

o Chemical abstract service number

o OSHA permissible exposure limit

o Threshold limit value

o Other exposure limits

• Physical and chemical characteristics o Boiling point

o Specific gravity

o Vapor pressure

o Melting point

o Vapor density

o Evaporation rate

o Solubility in water

o Appearance and odor

• Fire and explosion hazard data o Flash point

o Flammable limit

o Extinguishing media

o Special fire-fighting procedures

o Unusual fire and explosion hazard

• Reactivity data o Stability

o Incompatibility

o Hazardous decomposition or by-products

o Hazardous polymerization

• Health Hazard data o Routes of entry

o Health hazards (acute or chronic)

o Carcinogenicity

o National Toxicology Program (NTP)

o International Agency for Research on Cancer (IARC)

o Cal/OSHA regulated

o Signs and symptoms of exposure

o Medical conditions aggravated by exposure

o Emergency and first aid procedures

• Precautions for safe handling and use

o Steps to be taken in case of a spill or release

o Waste disposal methods

o Handling and storing precautions

o Other precautions

• Control measures

o Respiratory requirement, if needed

o Ventilation needed

o Protective gloves

o Eye protection

o Work/hygienic practices

Unfortunately, not all MSDS pages have a standard content format or look alike. Each manufacturer produces MSDS forms according to their own preferences and provides only the information the manufacturer believes is applicable to their product. While certain information may not be published by the manufacturer, MSDS documents provide a quick overview of the product’s characteristics and hazards. Therefore, it is necessary to verify product hazards using a minimum of two other sources of information about the chemical and its hazards before taking mitigation actions for spills, releases or fire incidents.

References

• IFSTA. (2009). Fire Inspection and Code Enforcement. Stillwater, OK: Fire Protection Publications (p. 585-603).

• State of California. (2010). California Fire Code. Sacramento, CA: California Building Standards Commission. (ch. 27 and 34).

5-3 Wildland Urban Interface

State of California WUI Regulations

Introduction

Wildfires are extremely costly to property owners, residents, and local agencies. The fire front is not the only source of risk; embers and firebrands travel far beyond the area impacted by the fire front, posing an ignition threat to structures or fuels over a longer period of time.

Since fires ignore jurisdictional boundaries, it is necessary that cities, counties, special districts, state agencies, and federal agencies develop the preventive measures necessary for public safety.

The prevention of wildland fires is not strictly a municipal matter, but a matter of statewide concern. The state's Wildland Urban Interface (WUI) regulations are found in the California Fire Code, CCR Titles 14 and 19, California Government Code, and the California Public Resource Code.

These regulations classify land types in California and allow local public officials to identify and require mitigation measures that will retard the rate of spread and reduce the potential intensity of uncontrolled fires that threaten to destroy resources, life, or property. None of the regulations limit the authority of a local agency to impose more restrictive fire and public safety requirements.

Definitions

Local Agency Very High Fire Hazard Severity Zone: An area designated by a local agency upon the recommendation of the CDF Director pursuant to Government Code Sections 51177(c), 51178 and 5118 that is not a state responsibility area and where a local agency, city, county, city and county, or district is responsible for fire protection.

State Responsibility Area (SRA):  Lands that are classified by the Board of Forestry pursuant to Public Resource Code Section 4125 where the financial responsibility of preventing and suppressing forest fires is primarily the responsibility of the state.

Wildland Urban Interface Fire Area: A geographical area identified by the state as a "Fire Hazard Severity Zone" in accordance with the Public Resource Code Sections 4201 through 4204 and Government Code Sections 51175 through 51189, or other areas designated by the enforcing agency to be at a significant risk from wildfires. See Section 706A for the applicable referenced sections of the Government Code and the Public Resource Code.

Vegetation Management And Fuel Modification Zones

The intent of fuel modification standards is to:

• Reduce the intensity of a wildfire by reducing the volume and density of flammable vegetation

• Increase the safety of emergency fire equipment and evacuating civilians

• Provide a point of attack or defense from a wildfire

California Code of Regulations, Title 14

Article 3 of Title 14 specifies minimum fire hazard reduction practices around buildings and structures in State Responsibility Areas. The intent of Article 3 is to provide guidance for implementation of Public Resource Code 4291(a) and (b), and to minimize the spread of fire within a 100-foot zone around a building or structure.

Any person who owns, leases, controls, operates, or maintains a building or structure in, upon, or adjoining any mountainous area, forest-covered lands, brush-covered lands, grass-covered lands, or any land that is covered with flammable material, and is within State Responsibility Area shall:

• Provide and maintain a firebreak within 30 feet from each building or structure by	 removing and clearing away all flammable vegetation and other combustible growth. Single specimens of trees or other vegetation may be kept if they are well spaced, well pruned, and create a condition that avoids spread of fire to other vegetation or to a building or structure.

• Provide and maintain a fuel break within the "Reduced Fuel Zone" (30 feet to 100 feet

from each building or structure, or to the property line, whichever is closer to the

structure), by disrupting the vertical and / or horizontal continuity of flammable and

combustible vegetation. This will reduce fire intensity, inhibit fire reaching the crowns of

trees, reduce the rate of fire spread, and provide a safer environment for fire fighters to

suppress wildfires.

All vegetation identified as a fire hazard shall be removed or modified when required by the Authority Having Jurisdiction.

Title 19 of the California Code of Regulations, Government Code Section 51175-51189 and Public Resources Code 4291

Title 19 applies to both SRA and LRA lands. The provisions of Government Code Sections 51175 though 51189 (LRA) and California Public Resources Code 4291 (SRA) contain similar, if not identical, requirements.

In general, no combustible material shall be placed or stored within 10 feet of any building or structure.

Any person who owns, leases, controls, operates, or maintains any building or structure in, upon, or adjoining any mountainous area or forest-covered lands, brush covered lands, or grass-covered lands, or any land which is covered with flammable material shall, at all times, do all of the following:

• Maintain a firebreak by removing and clearing all flammable vegetation or combustible growth for a minimum of 30 feet around each side of the building (or to the property line, whichever is nearer). This does not apply to single specimens of trees, ornamental shrubbery, or similar plants, which are used as ground cover, if they do not form a means of rapidly transmitting, fire from the native growth to any building or structure.

• Maintain a firebreak around all buildings by removing all brush, flammable vegetation, or combustible growth located between 30 and 100 feet (or to the property line, whichever is nearer) from all buildings or structures, if the enforcing agency finds that a firebreak of only 30-feet around the buildings is not sufficient to provide reasonable fire safety.

Grass and other vegetation located more than 30 feet form such building or structure and less than 18-inches in height above the ground may be maintained where necessary to stabilize the soil and prevent erosion.

The amount of fuel modification performed must take into consideration the flammability of the structure as affected by the building material, the building's location, and type of vegetation present. Fuels shall be maintained in a condition so that a wildfire burning under average weather conditions would be unlikely to ignite the structure.

Government Code 51182 is more restrictive than Title 19 and requires a minimum defensible space of 100 feet around all structures. Both the government and Public Resource Code restrict an insurance company's ability to require more than 100 feet of defensible space around buildings and limits fuel modification beyond property lines under specific guidelines. A property owner is not required to manage fuels on off-site lands if they do not have the legal right to manage those fuels, nor is anyone required to alter vegetation owned by another person.

The requirements of Government Code Section 51182 do not apply to any land used for one or more of the following purposes:

• Habitats for endangered or threatened species

• Lands kept in a natural state for wildlife, plant, or animal habitats

• Environmentally sensitive open space lands

• Remove any portion of a tree that is within 10 feet of a chimney or stovepipe.

• Cut and remove all dead or dying portions of trees next to or overhanging any building.

• Maintain the roof of any structure free of leaves, needles, or other dead vegetative growth.

• Provide and maintain at all times a screen over the outlet of every chimney or stovepipe that is attached to any fireplace, stove, or other device that burns any solid or liquid fuel. The screen shall be constructed of nonflammable material with openings of not more than one half inch in size.

California Code Requirements

Regulations found in the California Fire Code apply to both SRA and LRA lands.

Weeds, grass, vines, or other growth that is capable of being ignited and endangering property, must be cut down and removed by the owner or occupant of the premises. The Fire Code requires management of all hazardous vegetation according to the standards found in the Government Code, the Public Resources Code, and Titles 14 and 19.

Fire Apparatus Access Requirements

Title 14 Requirements and the California Fire Code have overlapping requirements for Fire Apparatus Access Roads. Public and private road networks must provide safe access for emergency wildland fire equipment and civilian evacuation, and shall provide unobstructed traffic circulation during a wildfire emergency.

Title 14 requires that all roads in SRA provide a minimum of two nine-foot traffic lanes for two-way traffic flow unless local jurisdictions have more stringent access requirements. Roads must be able to provide unobstructed access to conventional drive vehicles and shall be capable of supporting a 40,000-pound load.

Driveways shall provide a traffic lane with a minimum of 10 feet in width and unobstructed vertical clearance of 15 feet along its entire length. A turnaround shall be provided at all building sites on driveways over 300 feet in length, and shall be within 50 feet of the building.

If a driveway is serviced by a gate, the gate entrance shall be at least two feet wider than the width of the traffic lane(s) serving the gate. All gates providing access from a road to a driveway shall be located at least 30 feet from the roadway and shall open to allow a vehicle to stop without obstructing traffic on that road.

In SRA and LRA, the Fire Code requires that an approved Fire Apparatus Access Road be provided for every facility, building, or portion of building constructed or moved into the jurisdiction. The Fire Apparatus Access Road must extend to within 150 feet of all portions of the first story exterior walls of the building.

Premises Identification

Sections 1274 of Title 14 and 505 of the California Fire Code require that all new an existing

buildings have a permanently posted and visible address to avoid response delays and

facilitate locating fires. Approved address numbers shall contrast with their background,

have Arabic numerals or alphabet letters with a minimum height of 4 inches and a

minimum stroke width of 0.5 an inch.

The address must be placed at each driveway entrance and visible from both directions of travel along the road. Address signs along one-way roads shall be visible from both the intended direction of travel and the opposite direction. Where multiple addresses are required at a single driveway, they shall be mounted on a single post.

Incinerators

Section 603 of the California Fire Code requires all commercial, industrial, and residential-type incinerators and chimneys to be constructed as regulated by the California Building and Mechanical Codes. All incinerators must have effective spark arrestors and burning may only take place during approved hours.

If the fire code official determines that burning in incinerators located within 500 feet of mountains, brush, or grass-covered areas creates an undue fire hazard because of atmospheric conditions, burning shall be prohibited. The fire code official can require immediate discontinuance of incinerator use if they determine that smoke emissions are offensive to occupants of surrounding property or if the use of incinerators constitutes a hazardous condition.

References

• State of California. (2010). California Fire Code. Sacramento, CA: California Building Standards Commission.

• State of California. California Government Code. Retrieved from http://www.leginfo.ca.gov/.html/gov_table_of_contents.html on December 31, 2012.

• State of California. California Public Resource Code. Retrieved from http://www.leginfo.ca.gov/.html/prc_table_of_contents.html on December 31, 2012.

ACTIVITIES

Activity 2-1

Relationship between Historic and Modern Fire Problems

Acti                                              Format: Group

Timeframe: 1:30 (45 minutes reading and discussion / 45 minutes presentation)

D

Description:   This activity provides students with an opportunity to recognize the historic fire problems in today’s occupancies.

Ma                                 Materials:  Historic fire articles focused on the following occupancies: Assembly, Industrial, High rise, Educational;  Modern fire articles focused on the following occupancies: Assembly, Industrial,  High rise, Educational; Fire Hazard Worksheet (FHW) from Activity 2-1-1; Pen or pencil

In                                  Instructions

1. Working in groups, read about a historical and modern fire in a particular occupancy

2. Discuss the deficiencies that led to a fire loss

3. Individually, complete the Fire Hazard Worksheet for the assigned occupancy

4. Choose a group spokesperson and be prepared to discuss your answers with the class

Activity 2-2

Identifying Civilian Fire Death Trends

Format: Individual

Timeframe: 00:30 minutes

Description: This activity provides students with the opportunity to identify fire and life safety trends that influence civilian fire fatalities.

Materials Needed: U.S. Fire Administration annual Civilian Fire Fatalities reports (see pages 13-18); pen & pencil.

Instructions:

1. Work individually

2. Using the USFA Civilian Fire Fatality Reports, identify any trends that Company Inspections could address that would reduce loss of life.

3. Be prepared to discuss your answers with the class

Optional Activity 2-3

Community Risk Assessments

Format: Group

Timeframe: 1:30 minutes

Description: This activity provides students with the opportunity to develop a Community Risk Profile, write a problem statement, prioritize issues, identify Target audiences and hazards and identify intervention strategies

Materials Needed: U.S. Fire Administration annual Civilian Fire Fatalities reports (see pages 13-18); pen & pencil.

Instructions:

- You will be divided two groups.

- Given a scenario on community demographics and fire trends, follow the instructions provided in the scenario.

- You have 45 minutes to develop a Community Risk Profile, write a problem statement, prioritize problems, identify target hazards and audiences and identify intervention strategies.

Activity 2-5

Introduction to the California Fire Inspector's Guide

Format: Individual

Timeframe: 00:30

Description : This activity provides students with an opportunity to utilize the California Fire Inspector’s Guide to cite various violations with a code section for the California Fire Code (CFC).

Materials: California Fire Inspector’s Guide; Fire Hazard Worksheet (FHW) from Activity 2-1; Pen or pencil

Instructions

1. Work individually

2. Using your group’s assigned fire from Activity 2-1, identify the occupancy classification of the structure where the historic and modern fires occurred

3. Find a code section citation in the California Fire Inspector’s Guide for each deficiency recorded on the Fire Hazard Worksheet

| 4. Be prepared to discuss your answers with the class |  |
| --- | --- |
| c of 1 |  |
| Activity 3-2 Interior Finish Exercise Format: Group Timeframe: 00:30 Description : This activity provides students with an opportunity to evaluate how the Interior Finish characteristics in a Group A-2 Dining Occupancy will impact potential fire behavior Materials: California Fire Inspector’s Guide; 2013 California Fire Code Table 803.3; Reported Flame Spread Indices table Inspection Scenario: Your agency has received a complaint from a concerned citizen about a new restaurant that just opened in your Initial Attack Area. You observe the Interior Finish conditions as shown in the photograph below. The building owner provides you with a Consultant’s report that states that all of the decorative materials are “perfectly legal” and amenable for fire and life safety and the ambience of the dining facility (wood products highlighted in red on Flame Spread table). In 30 minutes, the Chief wants a report on the conditions you found and any recommendations you may have for mitigating the situation. Instructions 1. Work in the Groups you were assigned to for Activity 2-1. 2. Using the photograph of the occupancy (Group A-2 Restaurant), the California Fire Inspector’s Guide and CFC Table 803.3, prepare a summary of your findings, any violations you identified and corrective action to be taken. 3. Identify any potential political ramifications that may result from your inspection - Be prepared to discuss your answers with the class California Fire Code Flame Spread Index Requirements Activity 4-2 Performing Exterior Company Inspections Format: Group Timeframe: 1:00 (45 minutes activity / 15 minutes presentation) Description: This activity provides students with an opportunity to evaluate an assigned occupancy in the immediate vicinity for a reasonable degree of fire and life safety. Materials: An inspection form for the student’s department (or provided by instructor); • California Fire Inspector’s Guide: Pen or pencil Instructions: 1. In small groups of 4-6 persons, conduct an inspection of the exterior of the classroom building 2. Record the group’s findings on the fire inspection form 3. Be prepared to discuss your answers with the class Activity 4-3 Performing Interior Company Inspections Format: Group Timeframe: 1:00 (45 minutes activity / 15 minutes presentation) Description: This activity provides students with an opportunity to evaluate an assigned occupancy in the immediate vicinity for a reasonable degree of fire and life safety. Materials: An inspection form for the student’s department (or provided by instructor); • California Fire Inspector’s Guide: Pen or pencil Instructions: 1. In small groups of 4-6 persons, conduct an inspection of the interior of a _____ building 2. Record the group’s findings on the fire inspection form 3. Be prepared to discuss your answers with the class Activity 4-6 Code Enforcement Violation Rating Format: Individual Timeframe: 00:30 Description: This activity provides students with an opportunity to recognize the code enforcement rating of each deficiency in order to determine a code enforcement procedure (i.e., abatement, red tag, correction notice, etc.). Materials: A Fire Hazard Worksheet (FHW) from Activity 2-1; Pen or pencil Instructions 1. Work individually 2. Using your group’s assigned fire from Activity 2-1, review each deficiency and indicate if it is: a. Routine b. Imminent c. Transient 3. Be prepared to discuss options and methods for mitigation or correction of specific deficiencies with the class |  |

Activity 5-2-1

MSDS Information Search

Format: Group

Timeframe: 00:30

Description: This activity provides students with an opportunity to apply CFC requirements to a common field scenario.

Materials:  California Inspector’s Guide: a Fire Hazard Worksheet (FHW) from Activity 2-1;  Pen or pencil

Instructions:

- Working in groups, read the field inspection scenario.

- Answer the questions for each “issue” and list them on a separate sheet of paper.

- Using the answers from the hints, determine at least three violations.

- Find a Code section in the California Inspector’s Guide that prohibits the activity and record them.

- List any corrective actions necessary for each violation.

- You have 20 minutes to complete the activity.

- Be prepared to discuss your findings with the class.

Scenario:

You go to the Acme Automotive Paint Company for your annual fire inspection. While conducting the inspection, you see 1000 gallons of acrylic enamel reducer stored in five gallon containers displayed in the showroom of the store and 1100 gallons of enamel paint stored in one gallon cans. In addition, stored on 8 foot high wooden shelves in the sales area, you find 1500 gallons of lacquer retarder in 1 and 5 gallon metal cans. The exit door has cans of paint stored on both sides.

In a small outbuilding, you find a 55 gallon drum placed on its side. It has a quarter-turn valve on a spigot and is used to fill 1 and 5 gallon cans with a gun cleaner for customers.

The building is a Type III construction, 25,000 square foot mercantile occupancy with a sprinkler system with a discharge rate of 0.16 gpm per square foot over a 2500 square foot design area (Ordinary Hazard, Group 1).

_____________________________________________

Issue 1:

What is the classification of each material stored?

Acrylic enamel reducer (Flashpoint – 9 degrees F)

Enamel paint (FP -

Lacquer Retarder

Gun Cleaner

Issue # 2:

What is the maximum quantity of ignitable liquids allowed in a mercantile occupancy?

Issue # 3

Are all of the materials stored in accordance with the Fire Code?

Issue # 4

Is the dispensing of ignitable liquids in accordance with the Fire Code?

Activity 5-2-2

NFPA 704 Placards

Format: Individual

Timeframe: 00:30

Description: This activity provides students with an opportunity to determine the appropriate designations for a NFPA 704 placard.

Instructions

- Work individually

- Using the information given to you in each question, fill in the appropriate ratings for the NFPA placards

- You have 20 minutes to complete the activity

- Be prepared to discuss your answers with the class.

- A warehouse containing a flammable solid

- A structure storing a toxic substance

- A hospital outbuilding containing liquid oxygen

- A shed containing a water reactive 3 material

- A warehouse containing a Class III-A and Class I-A liquid

- A repair garage containing Class II liquids, Class I-C liquids and an oxy-acetylene welding torch.

- A chemical warehouse containing an organic peroxide II, a corrosive, a flammable cryogenic and a water reactive 3.