## Sheet1
STEAM CALC SHEET
[8 empty] | Known kW convert to kg/hour steam |  |  |  |  | kg/hour Steam = 3600 X kW |  |  |  |  | he = the specific Enthalpy of Evaporation at Steam working Pressure | [16 empty] | Approximate coefficients of friction
PROJECT |  | xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx | [12 empty] | he |  |  | SEE IOP Tables | [9 empty] | he
[24 empty] | 122 | kW |  |  | 2163.2 | [6 empty] | Materials |  | Static Friction, |  | Kinetic/Sliding Friction, | [7 empty] | Substance Name | Density | Specific Volume
[18 empty] | Current is pressure at 2 barg NEED to know what youre Working pressure is,. Adjust He accordingly | [18 empty] | Dry and clean | Lubricated | Dry and clean | Lubricated | [7 empty] | kg/m^3 | m^3/kg
[13 empty] | STEAM FLOW AT 1 BAR(g) | [21 empty] | Aluminium | Steel | 0.61 |  | 0.47 [12] | [7 empty] | Air | 1.29 | 0.77
Pipe Sizing by Pressure Loss for Steam | [13 empty] | ENTER KNOWN VALUES | [6 empty] | in the yellow area's | [13 empty] | Alumina ceramic | Silicon Nitride ceramic |  |  |  | 0.004 (wet)[13] | [6 empty] | Ice | 916.7 | 0.00109
[35 empty] | BAM (Ceramic alloy AlMgB14) | Titanium boride (TiB2) | 0.04–0.05 [14] | 0.02 [15][16] | [8 empty] | Water (liquid) | 1000 | 0.001
[13 empty] | ms | : Steam Flow Rate (kg/h) | [5 empty] | = | 203.0325 | kg/hour |  | 0.056398 | l/s | Kg/sec | [8 empty] | Brass | Steel | 0.35-0.51[12] | 0.19[12] | 0.44[12] | [7 empty] | Salt Water | 1030 | 0.00097
[13 empty] | l | : Pipe Length (m) | [5 empty] | = | 29 | metres length | [12 empty] | Cast iron | Copper | 1.05 |  | 0.29 [12] | [7 empty] | Mercury | 13546 | 7e-05
[13 empty] | d | : Pipe Inner Diameter (m) | [5 empty] | = | 0.08 | metre dia | NOT mm | [11 empty] | Cast iron | Zinc | 0.85[12] |  | 0.21[12] | [7 empty] | R-22* | 3.66 | 0.273
[13 empty] | v | : Steam Velocity (m/s) | [5 empty] | = | 13.9199 | m/s | [12 empty] | Concrete | Rubber | 1 | 0.30 (wet) | 0.6-0.85[12] | 0.45-0.75 (wet)[12] | [6 empty] | Ammonia | 0.769 | 1.3
[13 empty] | ∆p | : Pressure Loss (Pa) | [5 empty] | = | 3051.5485 | pa | [12 empty] | Concrete | Wood | 0.62[17] | [9 empty] | Carbon Dioxide | 1.977 | 0.506
[13 empty] | μ | : Coefficient of friction | [5 empty] | = | 0.16 | Constant | [12 empty] | Copper | Glass | 0.68 | [9 empty] | Chlorine | 2.994 | 0.334
|  | Ration of compression X internal pipe dia = pd calcs | [10 empty] | V | : Specific volume (m³/kg) | [5 empty] | = | 1.24 | Constant | [12 empty] | Copper | Steel | 0.53 |  | 0.36 [12] | [7 empty] | Hydrogen | 0.0899 | 11.12
|  | 8 bar | [32 empty] | Glass | Glass | 0.9-1.0[12] |  | 0.4 [12] | [7 empty] | Methane | 0.717 | 1.39
|  | 2.97 | X | 0.08 | = | 0.2376 | [28 empty] | Human synovial fluid | Cartilage |  | 0.01 [18] |  | 0.003 [18] | [6 empty] | Nitrogen | 1.25 | 0.799
[13 empty] | Pipe diameter |  |  |  | = | 0.08 | mm | = | Radius of |  | 0.04 | mm | X Squared = |  |  | 0.0016 | X | 3.14 | = | 0.005024 |  |  | Ice | Ice | 0.02-0.09[19] | [9 empty] | Steam* | 0.804 | 1.24
[6 empty] | inc. Below | [23 empty] | pi |  |  |  |  | Polyethene | Steel | 0.2[12][19] | 0.2[12][19]
| K X L X l/sSQrd | [5 empty] | 800 X L = | 23200 | X | 0.0031807 | = | [5 empty] | d | 2 X Ԓ | [16 empty] | PTFE (Teflon) | PTFE (Teflon) | 0.04[12][19] | 0.04[12][19] |  | 0.04[12]
| Comp ratio X inner pipe dia | [7 empty] | 0.2376 |  | 0.0031058 | [5 empty] | 2 | [17 empty] | Steel | Ice | 0.03[19]
[35 empty] | Steel | PTFE (Teflon) | 0.04[12]-0.2[19] | 0.04[12] |  | 0.04[12]
[35 empty] | Steel | Steel | 0.74[12]-0.80[19] | 0.16[19] | 0.42-0.62[12]
[35 empty] | Wood | Metal | 0.2–0.6[12][17] | 0.2 (wet)[12][17]
| Δp | = | 0.16 | X | 29 | X | 193.7628 |  |  |  | 899.0594 |  |  |  | Pascals | [19 empty] | Wood | Wood | 0.25–0.5[12][17] | 0.2 (wet)[12][17]
[9 empty] | = |  |  |  | = |  | 3051.5485 | Total pressure loss |  |  |  |  | 0.030515 | bar | ACTUAL PRESSURE LOSS
Adj for PRESSURE / Comprtession Ratio
|  |  |  | 0.2376 | X | 1.24 |  |  |  |  | 0.29462
| v | = |  | 203.0325 |  | 1.24 |  |  | = |  | 0.056398 | X | 246.8153 |  | = | 13.9199 | Steam Velocity m/s |  |  |  | Velocity CHECK | [13 empty] | RATIO of Compression,.
[5 empty] | X | [27 empty] | BAR g
[33 empty] | 0.5 | 1 | 2 | 3 | 4 | 5 | 5.5 | 6 | 7 | 8 | 10 | 12 | 14 | 18
|  |  |  | 3600 |  | 0.005024
[33 empty] | 1.5 | 1.99 | 2.97 | 3.96 | 4.95 | 5.94 | 6.43 | 6.92 | 7.91 | 8.9 | 10.87 | 12.85 | 14.82 | 18.77
| Pipe Sizing by Velocity for Steam | [43 empty] | 16
[43 empty] | 16.795 |  | 16.795
SQRoot of
[12 empty] | d | = |  | 0.056398 | X | 0.089081 | X | 1.2739 | [23 empty] | 15.8075 |  | 15
15.8075
PIPE SIZE mm
[14 empty] | SQRoot of |  | 0.0064 | = | 0.08 | mm |  | Pipe sizing CHECK |  |  | 80 | mm
SQRT ( Number )
Steam Pressure Loss through Piping
[14 empty] | 0.056398 | X | 1.24 |  | = |  | 0.056398 | X | 246.8153 |  | = |  | 13.9199 | m/s
0.005024
[13 empty] | d | : Pipe Inner Diameter (m) |  |  | 0.08
[13 empty] | v | : Steam Velocity (m/s) |  |  | 13.9199
[13 empty] | ms | : Steam Flow Rate (kg/h) |  |  | 203.0325
[13 empty] | V | : Specific volume (m³/kg) |  |  | 1.24
[11 empty] | Ms = |  | 0.069933 | [7 empty] | Kg/hour
[5 empty] | 0.04 | [8 empty] | X | 3600 |  | = |  |  |  | 203.0325
1.24
0.0016
0.005024
0.069933
STEAM FLOW AT 12.5 or xxxxx BAR(g) ADJUSTED for PRESSURE for REQUIRED PIPE SIZE
Alternatively the pipe size can be calculated arithmetically. The following information is required, and the procedure used for the calculation is outlined below.
ADJUSTED FOR PRESSUE
[8 empty] | vg = | 0.146 | 15 bar
| Information required to calculate the required pipe size: | [6 empty] | vg = | 0.17 | 12.5 bar
[9 empty] | 0.194 | 10
| u | = | Flow velocity (m/s) |  |  |  |  | vg = | 0.24 | 8 bar |  | pi | = |  | 3.14
| vg | = | Specific volume (m³/kg) |  |  |  |  | vg = | 0.27 | 7 bar
| Ms | = | Mass flowrate (kg/s) |  |  |  |  | Ms = | 0.056398 | kg/SECond |  |  | u | = | 13.9199 | X pi = | 43.7084
| Ѷ | = | Volumetric flowrate (m³/s) = ms x vg
| From this information, the cross sectional area (A) of the pipe can be calculated: | [11 empty] | Ѷ | = | 0.0095876 | X 4 = | 0.038351
| Rearranging the formula to give the diameter of the pipe (D) in metres: | [10 empty] | Ms X vg
[14 empty] | = | 0.038351 |  | SQRT of
[16 empty] | = | 0.00087742 |  | = |  | 0.029621 | metre
[14 empty] | = | 43.7084 |  |  |  | = |  | 29.6213 | mm |  | = SAY 500 mm Steam pipe Header to USE
AS AT
03 06 2015
[20 empty] | PIPE ADJ AT |  | 12.5 |  |  | CDB
bar(g)