## Home
repeating distances for various modules in inches
Inter-Row Spacing Calculator by Sean White www.pvstudent.com
|  |  |  | Flat with 1" spacing | 5 degrees | 10 degrees | 15 degrees | 20 degrees | Powerguard (SPR only)
Enter Module Width & Tilt Angle Only (yellow boxes)
Calculate Height of Module |  |  | SPR 305 | 42.18 | 65.2954 | 59.5651 | 68.112 | 76.1404 | 42.44
|  |  | ET 280 | 40.1 | 48.0109 | 56.5565 | 64.6716 | 72.2946 | n/a
module width | 39.1 | inches
tilt angle | 10 | degrees
sine tilt angle | 0.17365
height of module | 6.7896 | inches
Calculate Space Under Module
cosine tilt angle | 0.98481
space under module | 38.506 | inches
Calculate Shadow Length
Altitude Angle of Sun 9am 12-21 toronto | 12 | degrees
tangent of altitude angle | 0.21256
shadow length at 9am angle | 31.9428 | inches
Calculate Inter-Row Spacing
9am, 12/21 Azimuth from South at Latitude 43.5 | 33 | degrees
cosine of azimuth correction angle | 0.83867
inter-row space | 26.7895
Repeating Distance of Rows | 65.2954 | inches
Percent Increase in Space Needed for Same Amount of Modules Due To Shading
Verses Flat with 1" Spacing | 62.83%
Verses Flat with no Spacing | 67%
Verses PowerGuard Spacing (1.26") | 61.78%

## kWh per sq ft
Calculating Production and STC watts per unit area |  | by Sean White
Module | SPR 305
watts | 305
width (inches) | 41.18
height (inches | 61.39
area (sq in) | 2528.0402
area (sq ft) | 17.5558
STC watts/sq ft | 17.3731
flat with 1" spacing
area (sq in) | 2631.6102
area (sq ft) | 18.2751
STC watts/sq ft | 16.6894
STC kW/sq ft | 0.016689
STC watts/100 sq ft | 1668.9402
kW DC/100 sq ft (roofing square) | 1.6689
kW DC/1000 sq ft | 16.6894
annual kWh/kW STC | 1319.6066
annual kWh/sq ft | 22.0234
5 degree tilt
extra space required over flat with 1" spacing | 19.88%
conversion factor | 1.1988
STC watts per sq ft | 13.9219
STC kW/sq ft | 0.013922
kW DC/100 sq ft | 1.3922
kW DC/1000 sq ft | 13.9219
annual kWh/kW STC | 1381.1148
annual kWh/sq ft | 19.2277
10 degree tilt
extra space required over flat with 1" spacing | 41.22%
conversion factor | 1.4122
STC watts per sq ft | 11.8183
STC kW/sq ft | 0.011818
kW DC/100 sq ft | 1.1818
kW DC/1000 sq ft | 11.8183
annual kWh/kW STC | 1431.377
annual kWh/sq ft | 16.9165
15 degree tilt
extra space required over flat with 1" spacing | 61.48%
conversion factor | 1.6148
STC watts per sq ft | 10.3353
STC kW/sq ft | 0.010335
kW DC/100 sq ft | 1.0335
kW DC/1000 sq ft | 10.3353
annual kWh/kW STC | 1470.7213
annual kWh/sq ft | 15.2004
20 degree tilt
extra space required over flat with 1" spacing | 80.51%
conversion factor | 1.8051
STC watts per sq ft | 9.2455
STC kW/sq ft | 0.0092455
kW DC/100 sq ft | 0.92455
kW DC/1000 sq ft | 9.2455
annual kWh/kW STC | 1499.082
annual kWh/sq ft | 13.8598

## Production VS Angle
Solar energy production differences in tilt angles on CSI EPBB calculator using
SMA America:SC250U (480V) inverter & 100 modules as standard |  |  | by Sean White
(increasing modules 10 fold on same inverter on EPBB calculator increases output linearly (10 fold).
SMA America:SC250U (480V) is CEC rated 97% efficient
< | module | < |  | module
| SPR 305 |  |  | ET 280
0 deg tilt angle (>6" standoff) |  | 0 deg tilt angle (>6" standoff)
STC DC rating | 305 | STC DC rating |  | 280
STC rating for 100 modules (watts) | 30500 | STC rating for 100 modules (watts) |  | 28000
STC kW/100 modules | 30.5 | STC kW/100 modules |  | 28
annual kWH/100 modules (from epbb calculator) | 40248 | annual kWH/100 modules (from epbb calculator) |  | 36855
annual kWH/kW installed | 1319.6066 | annual kWH/kW installed |  | 1316.25
5 deg tilt angle |  | 5 deg tilt angle
STC DC rating | 305 | STC DC rating |  | 280
STC rating for 100 modules (watts) | 30500 | STC rating for 100 modules (watts) |  | 28000
STC kW/100 modules | 30.5 | STC kW/100 modules |  | 28
annual kWH/100 modules (from epbb calculator) | 42124 | annual kWH/100 modules (from epbb calculator) |  | 38554
annual kWH/kW installed | 1381.1148 | annual kWH/kW installed |  | 1376.9286
10 deg tilt angle |  | 10 deg tilt angle
STC DC rating | 305 | STC DC rating |  | 280
STC rating for 100 modules (watts) | 30500 | STC rating for 100 modules (watts) |  | 28000
STC kW/100 modules | 30.5 | STC kW/100 modules |  | 28
annual kWH/100 modules (from epbb calculator) | 43657 | annual kWH/100 modules (from epbb calculator) |  | 39941
annual kWH/kW installed | 1431.377 | annual kWH/kW installed |  | 1426.4643
15 deg tilt angle |  | 15 deg tilt angle
STC DC rating | 305 | STC DC rating |  | 280
STC rating for 100 modules (watts) | 30500 | STC rating for 100 modules (watts) |  | 28000
STC kW/100 modules | 30.5 | STC kW/100 modules |  | 28
annual kWH/100 modules (from epbb calculator) | 44857 | annual kWH/100 modules (from epbb calculator) |  | 41024
annual kWH/kW installed | 1470.7213 | annual kWH/kW installed |  | 1465.1429
20 deg tilt angle |  | 20 deg tilt angle
STC DC rating | 305 | STC DC rating |  | 280
STC rating for 100 modules (watts) | 30500 | STC rating for 100 modules (watts) |  | 28000
STC kW/100 modules | 30.5 | STC kW/100 modules |  | 28
annual kWH/100 modules (from epbb calculator) | 45722 | annual kWH/100 modules (from epbb calculator) |  | 41803
annual kWH/kW installed | 1499.082 | annual kWH/kW installed |  | 1492.9643
PowerGuard
STC DC rating | 305
STC rating for 100 modules (watts) | 30500
STC kW/100 modules | 30.5
annual kWH/100 modules (from epbb calculator) | 39714
annual kWH/kW installed | 1302.0984
*yellow indicates field to enter data

## SPR 305 5 deg
Inter-Row Spacing Calculator by Sean White
Enter Module Width & Tilt Angle Only (yellow boxes)
Calculate Height of Module
module width | 41.18 | inches
tilt angle | 5 | degrees
sine tilt angle | 0.087156
height of module | 3.5891 | inches
Calculate Space Under Module
cosine tilt angle | 0.99619
space under module | 41.0233 | inches
Calculate Shadow Length
Altitude Angle of Sun 9am 12-21 Oakland | 15.5 | degrees
tangent of altitude angle | 0.27732
shadow length at 9am angle | 12.9418 | inches
Calculate Inter-Row Spacing
9am, 12/21 Azimuth from South at Latitude 37.8 | 42.5 | degrees (Oakland, CA)
cosine of azimuth correction angle | 0.73728
inter-row space | 9.5417
Repeating Distance of Rows | 50.565 | inches
Percent Increase in Space Needed for Same Amount of Modules Due To Shading
Verses Flat with 1" Spacing | 19.88%
Verses Flat with no Spacing | 22.79%
Verses PowerGuard Spacing (1.26") | 19.14%

## SPR 305 10 deg
Inter-Row Spacing Calculator by Sean White
Enter Module Width & Tilt Angle Only (yellow boxes)
Calculate Height of Module
module width | 41.18 | inches
tilt angle | 10 | degrees
sine tilt angle | 0.17365
height of module | 7.1508 | inches
Calculate Space Under Module
cosine tilt angle | 0.98481
space under module | 40.5544 | inches
Calculate Shadow Length
Altitude Angle of Sun 9am 12-21 Oakland | 15.5 | degrees
tangent of altitude angle | 0.27732
shadow length at 9am angle | 25.7851 | inches
Calculate Inter-Row Spacing
9am, 12/21 Azimuth from South at Latitude 37.8 | 42.5 | degrees (Oakland, CA)
cosine of azimuth correction angle | 0.73728
inter-row space | 19.0107
Repeating Distance of Rows | 59.5651 | inches
Percent Increase in Space Needed for Same Amount of Modules Due To Shading
Verses Flat with 1" Spacing | 41.22%
Verses Flat with no Spacing | 44.65%
Verses PowerGuard Spacing (1.26") | 40.35%

## SPR 305 15 deg
Inter-Row Spacing Calculator by Sean White
Enter Module Width & Tilt Angle Only (yellow boxes)
Calculate Height of Module
module width | 41.18 | inches
tilt angle | 15 | degrees
sine tilt angle | 0.25882
height of module | 10.6582 | inches
Calculate Space Under Module
cosine tilt angle | 0.96593
space under module | 39.7768 | inches
Calculate Shadow Length
Altitude Angle of Sun 9am 12-21 Oakland | 15.5 | degrees
tangent of altitude angle | 0.27732
shadow length at 9am angle | 38.4321 | inches
Calculate Inter-Row Spacing
9am, 12/21 Azimuth from South at Latitude 37.8 | 42.5 | degrees (Oakland, CA)
cosine of azimuth correction angle | 0.73728
inter-row space | 28.3351
Repeating Distance of Rows | 68.112 | inches
Percent Increase in Space Needed for Same Amount of Modules Due To Shading
Verses Flat with 1" Spacing | 61.48%
Verses Flat with no Spacing | 65.4%
Verses PowerGuard Spacing (1.26") | 60.49%

## SPR 305 20 deg
Inter-Row Spacing Calculator by Sean White
Enter Module Width & Tilt Angle Only (yellow boxes)
Calculate Height of Module
module width | 41.18 | inches
tilt angle | 20 | degrees
sine tilt angle | 0.34202
height of module | 14.0844 | inches
Calculate Space Under Module
cosine tilt angle | 0.93969
space under module | 38.6965 | inches
Calculate Shadow Length
Altitude Angle of Sun 9am 12-21 Oakland | 15.5 | degrees
tangent of altitude angle | 0.27732
shadow length at 9am angle | 50.7867 | inches
Calculate Inter-Row Spacing
9am, 12/21 Azimuth from South at Latitude 37.8 | 42.5 | degrees (Oakland, CA)
cosine of azimuth correction angle | 0.73728
inter-row space | 37.4439
Repeating Distance of Rows | 76.1404 | inches
Percent Increase in Space Needed for Same Amount of Modules Due To Shading
Verses Flat with 1" Spacing | 80.51%
Verses Flat with no Spacing | 84.9%
Verses PowerGuard Spacing (1.26") | 79.41%

## ET 280 5 deg
Inter-Row Spacing Calculator by Sean White
Enter Module Width & Tilt Angle Only (yellow boxes)
Calculate Height of Module
module width | 39.1 | inches
tilt angle | 5 | degrees
sine tilt angle | 0.087156
height of module | 3.4078 | inches
Calculate Space Under Module
cosine tilt angle | 0.99619
space under module | 38.9512 | inches
Calculate Shadow Length
Altitude Angle of Sun 9am 12-21 Oakland | 15.5 | degrees
tangent of altitude angle | 0.27732
shadow length at 9am angle | 12.2881 | inches
Calculate Inter-Row Spacing
9am, 12/21 Azimuth from South at Latitude 37.8 | 42.5 | degrees (Oakland, CA)
cosine of azimuth correction angle | 0.73728
inter-row space | 9.0597
Repeating Distance of Rows | 48.0109 | inches
Percent Increase in Space Needed for Same Amount of Modules Due To Shading
Verses Flat with 1" Spacing | 19.73%
Verses Flat with no Spacing | 22.79%
Verses PowerGuard Spacing (1.26") | 18.96%

## ET 280 10 deg
Inter-Row Spacing Calculator by Sean White
Enter Module Width & Tilt Angle Only (yellow boxes)
Calculate Height of Module
module width | 39.1 | inches
tilt angle | 10 | degrees
sine tilt angle | 0.17365
height of module | 6.7896 | inches
Calculate Space Under Module
cosine tilt angle | 0.98481
space under module | 38.506 | inches
Calculate Shadow Length
Altitude Angle of Sun 9am 12-21 Oakland | 15.5 | degrees
tangent of altitude angle | 0.27732
shadow length at 9am angle | 24.4827 | inches
Calculate Inter-Row Spacing
9am, 12/21 Azimuth from South at Latitude 37.8 | 42.5 | degrees (Oakland, CA)
cosine of azimuth correction angle | 0.73728
inter-row space | 18.0505
Repeating Distance of Rows | 56.5565 | inches
Percent Increase in Space Needed for Same Amount of Modules Due To Shading
Verses Flat with 1" Spacing | 41.04%
Verses Flat with no Spacing | 44.65%
Verses PowerGuard Spacing (1.26") | 40.13%

## ET 280 15 deg
Inter-Row Spacing Calculator by Sean White
Enter Module Width & Tilt Angle Only (yellow boxes)
Calculate Height of Module
module width | 39.1 | inches
tilt angle | 15 | degrees
sine tilt angle | 0.25882
height of module | 10.1198 | inches
Calculate Space Under Module
cosine tilt angle | 0.96593
space under module | 37.7677 | inches
Calculate Shadow Length
Altitude Angle of Sun 9am 12-21 Oakland | 15.5 | degrees
tangent of altitude angle | 0.27732
shadow length at 9am angle | 36.4909 | inches
Calculate Inter-Row Spacing
9am, 12/21 Azimuth from South at Latitude 37.8 | 42.5 | degrees (Oakland, CA)
cosine of azimuth correction angle | 0.73728
inter-row space | 26.9039
Repeating Distance of Rows | 64.6716 | inches
Percent Increase in Space Needed for Same Amount of Modules Due To Shading
Verses Flat with 1" Spacing | 61.28%
Verses Flat with no Spacing | 65.4%
Verses PowerGuard Spacing (1.26") | 60.24%

## ET 280 20 deg
Inter-Row Spacing Calculator by Sean White
Enter Module Width & Tilt Angle Only (yellow boxes)
Calculate Height of Module
module width | 39.1 | inches
tilt angle | 20 | degrees
sine tilt angle | 0.34202
height of module | 13.373 | inches
Calculate Space Under Module
cosine tilt angle | 0.93969
space under module | 36.742 | inches
Calculate Shadow Length
Altitude Angle of Sun 9am 12-21 Oakland | 15.5 | degrees
tangent of altitude angle | 0.27732
shadow length at 9am angle | 48.2214 | inches
Calculate Inter-Row Spacing
9am, 12/21 Azimuth from South at Latitude 37.8 | 42.5 | degrees (Oakland, CA)
cosine of azimuth correction angle | 0.73728
inter-row space | 35.5526
Repeating Distance of Rows | 72.2946 | inches
Percent Increase in Space Needed for Same Amount of Modules Due To Shading
Verses Flat with 1" Spacing | 80.29%
Verses Flat with no Spacing | 84.9%
Verses PowerGuard Spacing (1.26") | 79.12%